## GT_S23
Bilan
efficacité | énergie payante | énergie utile | T0 exergie
0.358 | 890 | 318 | 288.15
POINTS | 5
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
air inlet | air | 288.15 | 1 | 1 | -9.8704 | 0.12801 | 0.8273 | -7.0424 | -46.7568 | 1001.8778 | 714.77 | 1.4017
2 | air | 478.9117 | 5 | 1 | 183.2551 | 0.17969 | 0.275 | 131.314 | 131.4767 | 1028.0878 | 740.98 | 1.3875
3 | burnt gas | 1223.15 | 5 | 1 | 1049.931 | 1.335 | 0.71219 | 780.5922 | 665.2367 | 1235.5699 | 944.44 | 1.3083
exhaust | burnt gas | 873.206 | 1 | 1 | 629.4885 | 1.3994 | 2.5422 | 462.0289 | 226.2577 | 1163.8299 | 872.7 | 1.3336
fuel | CH4 ` methane | 288.15 | 5 | 1 | -21.759 | -0.82043 | 0.29866 | -16.6543 | 214.6489 | 2197.65 | 1679.41 | 1.3086
PROCESSES | 6
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
fuel | fuel | fuel | exchange | 0 | 0 | other | 0.013814
exhaust | exhaust | exhaust | exchange | 0 | 0 | other | 0.79381
air inlet | air inlet | air inlet | exchange | 0 | 0 | other | 0.78
compressor | air inlet | 2 | compression | 150.6379 | 139.0221 | useful | 0.78
turbine | 3 | exhaust | expansion | -333.753 | -348.4675 | useful | 0.79381
combustion chamber | 2 | 3 | combustion | 690.5105 | 425.5221 | purchased | 0.79381
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
compressor | 150.6379 | 150.6379 |  |  |  | 139.0221 | 11.6158 | 2.289%
turbine | -333.753 | -333.753 |  |  |  | -348.4675 | 14.7145 | 2.9%
combustion chamber | 690.5105 |  | 690.5105 |  | 690.5105 | 425.5221 | 264.9884 | 52.23%
intake / exhaust | [5 empty] | -216.0768 | 216.0768 | 42.59%
cycle | 507.3955 | -183.1151 | 690.5105 |  |  | 1.3043e-07 | 507.3955 | 100%
|  |  |  | sigma(xq+) |  | 690.5105
|  |  |  | sigma(tau+) |  | 0
energy efficiency |  | 26.52% | exergy efficiency |  | 26.52%
Note on F28: assuming that the fuel exergy is equal to its LHV
Note on H29: irreversibilties due to the release of hot gases in the atmosphere

## GT_S23_regen
Bilan
efficacité | énergie payante | énergie utile | T0 exergie
0.358 | 890 | 318 | 288.15
POINTS | 5
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
air inlet | air | 288.15 | 1 | 1 | -9.8704 | 0.12801 | 0.8273 | -7.0424 | -46.7568 | 1001.8778 | 714.77 | 1.4017
2 | air | 478.9117 | 5 | 1 | 183.2551 | 0.17969 | 0.275 | 131.314 | 131.4767 | 1028.0878 | 740.98 | 1.3875
3 | burnt gas | 1223.15 | 5 | 1 | 1032.8469 | 1.293 | 0.70827 | 764.9913 | 660.278 | 1212.1466 | 922.62 | 1.3138
exhaust | burnt gas | 573.2347 | 1 | 1 | 287.3021 | 0.89627 | 1.6597 | 207.6143 | 29.0427 | 1073.0766 | 783.55 | 1.3695
fuel | CH4 ` methane | 288.15 | 5 | 1 | -21.759 | -0.82043 | 0.29866 | -16.6543 | 214.6489 | 2197.65 | 1679.41 | 1.3086
5 | air | 791.3547 | 5 | 1 | 515.1207 | 0.71169 | 0.45441 | 373.4748 | 310.0471 | 1096.8678 | 809.76 | 1.3546
4 | burnt gas | 869.4654 | 1 | 1 | 615.6947 | 1.3571 | 2.5173 | 450.2403 | 224.6574 | 1143.2266 | 853.7 | 1.3391
PROCESSES | 8
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
regen gas | 4 | exhaust | exchange | -258.8552 | -154.1931 | other | 0.78825
regen | 2 | 5 | exchange | 258.8552 | 139.2849 | other | 0.78
fuel | fuel | fuel | exchange | 0 | 0 | other | 0.008249
exhaust | exhaust | exhaust | exchange | 0 | 0 | other | 0.78825
air inlet | air inlet | air inlet | exchange | 0 | 0 | other | 0.78
compressor | air inlet | 2 | compression | 150.6379 | 139.0221 | useful | 0.78
turbine | 3 | 4 | expansion | -328.8197 | -343.3775 | useful | 0.78825
combustion chamber | 5 | 3 | combustion | 412.3463 | 278.6267 | purchased | 0.78825
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
compressor | 150.6379 | 150.6379 |  |  |  | 139.0221 | 11.6158 | 4.961%
turbine | -328.8197 | -328.8197 |  |  |  | -343.3775 | 14.5578 | 6.217%
combustion chamber | 412.3463 |  | 412.3463 |  | 412.3463 | 278.6267 | 133.7196 | 57.11%
regen gas | -258.8552 |  | -258.8552 |  |  | -154.1931 | 14.9081 | 6.367%
regen | 258.8552 |  | 258.8552 |  |  | 139.2849
intake / exhaust | [5 empty] | -59.3632 | 59.3632 | 25.35%
cycle | 234.1645 | -178.1818 | 412.3463 |  |  | -2.237e-07 | 234.1645 | 100%
|  |  |  | sigma(xq+) |  | 412.3463
|  |  |  | sigma(tau+) |  | 0
energy efficiency |  | 43.21% | exergy efficiency |  | 43.21%
Note on F32: assuming that the fuel exergy is equal to its LHV
Note on H35: irreversibilties due to the release of hot gases in the atmosphere

## steam_S28
Balance
effectiveness | purchased energy | useful energy | T0 exergy
0.39 | 3360 | 1309 | 288.15
POINTS | 6
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
1 | water | 302.1326 | 0.04 | 0 | 121.4493 | 0.42262 | 0.001004 | 121.4453 | -0.32739 | 0 | 0 | 0
2 | water | 302.5061 | 169 | 0 | 138.3508 | 0.42262 | 0.00099673 | 121.506 | 16.5742 | 0 | 0 | 0
3a | water | 624.9307 | 169 | 0 | 1686.7129 | 3.8029 | 0.0017635 | 1656.9091 | 590.9196 | 0 | 0 | 0
3b | water | 624.9307 | 169 | 1 | 2555.5135 | 5.1933 | 0.0084689 | 2412.3895 | 1059.055 | 0 | 0 | 0
3 | water | 815.15 | 169 | 1 | 3405.791 | 6.4203 | 0.019749 | 3072.0345 | 1555.7867 | 0 | 0 | 0
4 | water | 302.1326 | 0.04 | 0.83554 | 2154.3895 | 7.1512 | 29.0787 | 2038.0749 | 93.7716 | 0 | 0 | 0
PROCESSES | 6
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
pump | 1 | 2 | compression | 4140.8639 | 4140.8912 | useful | 245
economiser | 2 | 3a | exchange | 379348.7274 | 140714.6272 | purchased | 245
evaporator | 3a | 3b | exchange | 212856.1476 | 114693.1767 | purchased | 245
superheater | 3b | 3 | exchange | 208317.9686 | 121699.2662 | purchased | 245
turbine | 3 | 4 | expansion | -306593.3478 | -358193.7035 | useful | 245
condenser | 4 | 1 | exchange | -498070.3597 | -23054.2579 | other | 245
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
condenser | -498070.3597 |  | -498070.3597 | 288.15 | 0 | -23054.2579 | 23054.2579 | 7.276%
superheater | 208317.9686 |  | 208317.9686 | 1273 | 161164.1409 | 121699.2662 | 39464.8747 | 12.45%
evaporator | 212856.1476 |  | 212856.1476 | 1273 | 164675.0801 | 114693.1767 | 49981.9033 | 15.77%
economiser | 379348.7274 |  | 379348.7274 | 1273 | 293481.2209 | 140714.6272 | 152766.5937 | 48.21%
pump | 4140.8639 | 4140.8639 |  |  |  | 4140.8912 | -0.02737 | -8.638e-06%
turbine | -306593.3478 | -306593.3478 |  |  |  | -358193.7035 | 51600.3556 | 16.28%
cycle | 0 | -302452.484 | 302452.484 |  |  | 9.9835e-09 | 316867.9579 | 100%
|  |  |  | sigma(xq+) |  | 619320.4419
|  |  |  | sigma(tau+) |  | 0
energy efficiency |  | 37.78% | exergy efficiency |  | 48.84%

## steam_reheat_S28
Bilan
efficacité | énergie payante | énergie utile | T0 exergie
0.423 | 3383 | 1430 | 288.15
POINTS | 10
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
1 | water | 302.1326 | 0.04 | 0 | 121.4493 | 0.42262 | 0.001004 | 121.4453 | -0.32739 | 0 | 0 | 0
2 | water | 302.1649 | 15 | 0 | 122.9508 | 0.42262 | 0.0010033 | 121.4458 | 1.1741 | 0 | 0 | 0
3a | water | 624.9307 | 169 | 0 | 1686.7129 | 3.8029 | 0.0017635 | 1656.9091 | 590.9196 | 0 | 0 | 0
3b | water | 624.9307 | 169 | 1 | 2555.5135 | 5.1933 | 0.0084689 | 2412.3895 | 1059.055 | 0 | 0 | 0
3 | water | 815.15 | 169 | 1 | 3405.791 | 6.4203 | 0.019749 | 3072.0345 | 1555.7867 | 0 | 0 | 0
4 | water | 503.079 | 15 | 1 | 2874.0904 | 6.6137 | 0.14444 | 2657.4312 | 968.357 | 0 | 0 | 0
B | water | 401.7995 | 169 | 0 | 551.9881 | 1.6046 | 0.001059 | 534.0913 | 89.6218 | 0 | 0 | 0
4a | water | 302.1326 | 0.04 | 0.97896 | 2503.3632 | 8.3062 | 34.0701 | 2367.0828 | 109.9246 | 0 | 0 | 0
3c | water | 815.15 | 15 | 1 | 3564.7151 | 7.6863 | 0.24835 | 3192.1834 | 1349.9044 | 0 | 0 | 0
A | water | 400.4396 | 15 | 0 | 535.6218 | 1.6046 | 0.0010667 | 534.0218 | 73.2553 | 0 | 0 | 0
PROCESSES | 10
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
reheat | 4 | 3c | exchange | 124450.5605 | 68754.8343 | purchased | 180.2
extraction | 4 | 4 | exchange | 0 | 0 | other | 31.8
pump | 1 | 2 | compression | 270.5772 | 270.5684 | useful | 180.2
economiser | B | 3a | exchange | 240561.6704 | 106275.1421 | purchased | 212
evaporator | 3a | 3b | exchange | 184185.7277 | 99244.708 | purchased | 212
superheater | 3b | 3 | exchange | 180258.8137 | 105307.1201 | purchased | 212
HP turbine | 3 | 4 | expansion | -112720.5101 | -124535.0995 | useful | 212
condenser | 4a | 1 | exchange | -429220.8929 | -19867.4123 | other | 180.2
LP turbine | 3c | 4a | expansion | -191255.6019 | -223444.3533 | useful | 180.2
feedwater pump | A | B | compression | 3469.656 | 3469.6913 | useful | 212
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
feedwater pump | 3469.656 | 3469.656 |  |  |  | 3469.6913 | -0.035274 | -1.398e-05%
pump | 270.5772 | 270.5772 |  |  |  | 270.5684 | 0.0088082 | 3.492e-06%
HP turbine | -112720.5101 | -112720.5101 |  |  |  | -124535.0995 | 11814.5894 | 4.683%
LP turbine | -191255.6019 | -191255.6019 |  |  |  | -223444.3533 | 32188.7515 | 12.76%
condenser | -429220.8929 |  | -429220.8929 | 288.15 | 0 | -19867.4123 | 19867.4123 | 7.876%
economiser | 240561.6704 |  | 240561.6704 | 1273 | 186109.3175 | 106275.1421 | 79834.1753 | 31.65%
extraction | 0 |  | 0 |  |  | 0 | 0 | 0%
reheat | 124450.5605 |  | 124450.5605 | 1273 | 96280.5456 | 68754.8343 | 27525.7113 | 10.91%
superheater | 180258.8137 |  | 180258.8137 | 1273 | 139456.3179 | 105307.1201 | 34149.1977 | 13.54%
evaporator | 184185.7277 |  | 184185.7277 | 1273 | 142494.355 | 99244.708 | 43249.647 | 17.14%
mixer | [5 empty] | -3633.9211 | 3633.9211 | 1.441%
cycle | 0.00063391 | -300235.8787 | 300235.8793 |  |  | 11841.278 | 252263.3791 | 100%
|  |  |  | sigma(xq+) |  | 564340.5359
|  |  |  | sigma(tau+) |  | 0
energy efficiency |  | 41.16% | exergy efficiency |  | 55.3%

## refrig_S32_25
Balance
effectiveness | purchased energy | useful energy | T0 exergy
4.06 | 40 | 162 | 308.15
POINTS | 5
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
1 | R12 | 277.3369 | 3 | 1 | 355.6373 | 1.571 | 0.058868 | 337.9769 | -112.7696 | 0 | 0 | 0
2 | R12 | 347.4726 | 12.45 | 1 | 390.8358 | 1.5973 | 0.015863 | 371.087 | -85.4131 | 0 | 0 | 0
3a | R12 | 324.1708 | 12.45 | 1 | 372.6431 | 1.5437 | 0.013909 | 355.3262 | -87.6062 | 0 | 0 | 0
3 | R12 | 319.1708 | 12.45 | 0 | 245.5022 | 1.1514 | 0.00081271 | 244.4904 | -97.7924 | 1120.5502 | 1051.79 | 1.0654
4 | R12 | 272.3369 | 3 | 0.30206 | 245.5022 | 1.1671 | 0.017884 | 240.1369 | -102.4669 | 0 | 0 | 0
PROCESSES | 5
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
refrigeration effect | 4 | 1 | exchange | 92.073 | -8.613 | useful | 0.836
condenser | 3a | 3 | exchange | -106.2898 | -8.5157 | other | 0.836
desuperheating | 2 | 3a | exchange | -15.2091 | -1.8334 | other | 0.836
compressor | 1 | 2 | compression | 29.426 | 22.87 | purchased | 0.836
throttling | 3 | 4 | throttling | 0 | -3.9079 | other | 0.836
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
refrigeration effect | 92.073 |  | 92.073 | 278 | -9.9856 | -8.613 | -1.3726 | -7.061%
condenser | -106.2898 |  | -106.2898 | 308.15 | 0 | -8.5157 | 8.5157 | 43.8%
desuperheating | -15.2091 |  | -15.2091 | 308.15 | 0 | -1.8334 | 1.8334 | 9.431%
compressor | 29.426 | 29.426 |  |  |  | 22.87 | 6.5559 | 33.72%
throttling | 0 | 0 |  |  |  | -3.9079 | 3.9079 | 20.1%
cycle | -92.073 | 29.426 | -121.4989 |  |  | 0 | 19.4403 | 100%
|  |  |  | sigma(xq+) |  | 0
|  |  |  | sigma(tau+) |  | 29.426
energy efficiency |  | 3.129 | exergy efficiency |  | 33.93%

## refrig_S32_35
Balance
effectiveness | purchased energy | useful energy | T0 exergy
4.06 | 40 | 162 | 298.15
POINTS | 5
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
1 | R12 | 277.3369 | 3 | 1 | 355.6373 | 1.571 | 0.058868 | 337.9769 | -112.7696 | 0 | 0 | 0
2 | R12 | 335.5622 | 10 | 1 | 385.1446 | 1.5934 | 0.019557 | 365.5876 | -89.9157 | 0 | 0 | 0
3a | R12 | 314.8932 | 10 | 1 | 369.6315 | 1.5463 | 0.017544 | 352.0872 | -91.3945 | 0 | 0 | 0
3 | R12 | 309.8932 | 10 | 0 | 235.8973 | 1.1215 | 0.00078868 | 235.1086 | -98.4802 | 1090.8902 | 1022.13 | 1.0673
4 | R12 | 272.3369 | 3 | 0.23933 | 235.8973 | 1.1318 | 0.014319 | 231.6017 | -101.5565 | 0 | 0 | 0
PROCESSES | 5
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
refrigeration effect | 4 | 1 | exchange | 100.1027 | -9.3741 | useful | 0.836
condenser | 3a | 3 | exchange | -111.8018 | -5.9236 | other | 0.836
desuperheating | 2 | 3a | exchange | -12.9689 | -1.2363 | other | 0.836
compressor | 1 | 2 | compression | 24.6681 | 19.1058 | purchased | 0.836
throttling | 3 | 4 | throttling | 0 | -2.5718 | other | 0.836
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
refrigeration effect | 100.1027 |  | 100.1027 | 278 | -7.2556 | -9.3741 | 2.1185 | 12.17%
condenser | -111.8018 |  | -111.8018 | 298.15 | 0 | -5.9236 | 5.9236 | 34.02%
desuperheating | -12.9689 |  | -12.9689 | 298.15 | 0 | -1.2363 | 1.2363 | 7.1%
compressor | 24.6681 | 24.6681 |  |  |  | 19.1058 | 5.5623 | 31.94%
throttling | 0 | 0 |  |  |  | -2.5718 | 2.5718 | 14.77%
cycle | -100.1027 | 24.6681 | -124.7708 |  |  | 0 | 17.4124 | 100%
|  |  |  | sigma(xq+) |  | 0
|  |  |  | sigma(tau+) |  | 24.6681
energy efficiency |  | 4.058 | exergy efficiency |  | 29.41%

## heat_pump_S33
Balance
effectiveness | purchased energy | useful energy | T0 exergy
4.06 | 40 | 162 | 278.15
POINTS | 5
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
2 | propane | 338.4021 | 17 | 1 | 658.8401 | 2.4449 | 0.028871 | 609.7593 | -21.1995 | 0 | 0 | 0
3 | propane | 312.7918 | 17 | 0 | 306.8462 | 1.3566 | 0.0021325 | 303.221 | -70.493 | 3100.0732 | 2911.53 | 1.0648
3a | propane | 322.7918 | 17 | 1 | 622.0328 | 2.3341 | 0.025796 | 578.1798 | -27.2098 | 0 | 0 | 0
4 | propane | 267.7008 | 4 | 0.31526 | 306.8462 | 1.4002 | 0.037219 | 291.9585 | -82.6236 | 0 | 0 | 0
1 | propane | 272.7008 | 4 | 1 | 577.1446 | 2.4088 | 0.11681 | 530.4189 | -92.8535 | 0 | 0 | 0
ground return | prop. glycol water 30% | 280.15 | 1 | 0 | 26.6685 | 0.11467 | 0.00096785 | 26.6685 | -5.2272 | 4105.7197 | 3819.03 | 1.0751
ground departure | prop. glycol water 30% | 273.0549 | 1 | 0 | -0.36137 | -0.0015746 | 0.0009653 | -0.36137 | 0.076599 | 4086.9697 | 3800.28 | 1.0754
heating return | water | 308.15 | 1 | 0 | 146.6787 | 0.50499 | 0.0010059 | 146.5781 | 6.2168 | 0 | 0 | 0
heating | water | 315.6932 | 1 | 0 | 178.1974 | 0.60604 | 0.0010088 | 178.0965 | 9.6269 | 0 | 0 | 0
heating departure | water | 316.574 | 1 | 0 | 181.8781 | 0.61769 | 0.0010092 | 181.7772 | 10.069 | 0 | 0 | 0
PROCESSES | 12
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
heating departure | heating departure | heating departure | exchange | 0 | 0 | other | 1
heating 2 | heating | heating departure | exchange | 3.6807 | 0.44212 | other | 1
heating 1 | heating return | heating | exchange | 31.5187 | 3.4101 | other | 1
heating return | heating return | heating return | exchange | 0 | 0 | other | 1
ground departure | ground departure | ground departure | exchange | 0 | 0 | other | 1
cold source | ground return | ground departure | exchange | -27.0298 | 5.3038 | other | 1
ground return | ground return | ground return | exchange | 0 | 0 | other | 1
evaporator | 4 | 1 | exchange | 27.0298 | -1.023 | other | 0.1
condenser | 3a | 3 | exchange | -31.5187 | -4.3283 | useful | 0.1
desuperheater | 2 | 3a | exchange | -3.6807 | -0.60103 | useful | 0.1
compressor | 1 | 2 | compression | 8.1695 | 7.1654 | purchased | 0.1
throttling | 3 | 4 | throttling | 0 | -1.2131 | other | 0.1
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
evaporator | 27.0298 |  | 27.0298 | 276 | -0.21056 | -1.023 | 0.81243 | 19.82%
condenser | -31.5187 |  | -31.5187 | 312 | -3.4196 | -4.3283 | 0.90875 | 22.17%
desuperheater | -3.6807 |  | -3.6807 | 316 | -0.44087 | -0.60103 | 0.16016 | 3.908%
compressor | 8.1695 | 8.1695 |  |  |  | 7.1654 | 1.0041 | 24.5%
throttling | 0 | 0 |  |  |  | -1.2131 | 1.2131 | 29.6%
cycle | -27.0298 | 8.1695 | -35.1994 |  |  | 4.7e-08 | 4.0985 | 100%
|  |  |  | sigma(xq+) |  | 0
|  |  |  | sigma(tau+) |  | 8.1695
energy efficiency |  | 4.3086 | exergy efficiency |  | 49.83%

## heat_pump_S33_heating
Balance
effectiveness | purchased energy | useful energy | T0 exergy
4.06 | 40 | 162 | 278.15
POINTS | 5
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
2 | propane | 338.4021 | 17 | 1 | 658.8401 | 2.4449 | 0.028871 | 609.7593 | -21.1995 | 0 | 0 | 0
3 | propane | 312.7918 | 17 | 0 | 306.8462 | 1.3566 | 0.0021325 | 303.221 | -70.493 | 3100.0732 | 2911.53 | 1.0648
3a | propane | 322.7918 | 17 | 1 | 622.0328 | 2.3341 | 0.025796 | 578.1798 | -27.2098 | 0 | 0 | 0
4 | propane | 267.7008 | 4 | 0.31526 | 306.8462 | 1.4002 | 0.037219 | 291.9585 | -82.6236 | 0 | 0 | 0
1 | propane | 272.7008 | 4 | 1 | 577.1446 | 2.4088 | 0.11681 | 530.4189 | -92.8535 | 0 | 0 | 0
ground return | prop. glycol water 30% | 280.15 | 1 | 0 | 26.6685 | 0.11467 | 0.00096785 | 26.6685 | -5.2272 | 4105.7197 | 3819.03 | 1.0751
ground departure | prop. glycol water 30% | 273.0549 | 1 | 0 | -0.36137 | -0.0015746 | 0.0009653 | -0.36137 | 0.076599 | 4086.9697 | 3800.28 | 1.0754
heating return | water | 308.15 | 1 | 0 | 146.6787 | 0.50499 | 0.0010059 | 146.5781 | 6.2168 | 0 | 0 | 0
heating | water | 315.6932 | 1 | 0 | 178.1974 | 0.60604 | 0.0010088 | 178.0965 | 9.6269 | 0 | 0 | 0
heating departure | water | 316.574 | 1 | 0 | 181.8781 | 0.61769 | 0.0010092 | 181.7772 | 10.069 | 0 | 0 | 0
PROCESSES | 12
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
heating departure | heating departure | heating departure | exchange | 0 | 0 | other | 1
heating 2 | heating | heating departure | exchange | 3.6807 | 0.44212 | other | 1
heating 1 | heating return | heating | exchange | 31.5187 | 3.4101 | other | 1
heating return | heating return | heating return | exchange | 0 | 0 | other | 1
ground departure | ground departure | ground departure | exchange | 0 | 0 | other | 1
cold source | ground return | ground departure | exchange | -27.0298 | 5.3038 | other | 1
ground return | ground return | ground return | exchange | 0 | 0 | other | 1
evaporator | 4 | 1 | exchange | 27.0298 | -1.023 | other | 0.1
condenser | 3a | 3 | exchange | -31.5187 | -4.3283 | useful | 0.1
desuperheater | 2 | 3a | exchange | -3.6807 | -0.60103 | useful | 0.1
compressor | 1 | 2 | compression | 8.1695 | 7.1654 | purchased | 0.1
throttling | 3 | 4 | throttling | 0 | -1.2131 | other | 0.1
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
condenser | -31.5187 |  | -31.5187 | 312 | -3.4196 | -4.3283
desuperheater | -3.6807 |  | -3.6807 | 316 | -0.44087 | -0.60103
compressor | 8.1695 | 8.1695
heating circuit | 35.1994 |  | 35.1994 |  |  | 3.8522 | 1.0771
cycle | 8.1695 | 8.1695 | -1e-08
|  |  |  | sigma(xq+) |  | 0
|  |  |  | sigma(tau+) |  | 8.1695
energy efficiency |  | 4.3086 | exergy efficiency |  | 47.15%

## boiler_S33
Balance
effectiveness | purchased energy | useful energy | T0 exergy
4.06 | 40 | 162 | 278.15
POINTS | 5
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
heating return | water | 308.15 | 1 | 0 | 146.6787 | 0.50499 | 0.0010059 | 146.5781 | 6.2168 | 0 | 0 | 0
heating departure | water | 316.574 | 1 | 0 | 181.8781 | 0.61769 | 0.0010092 | 181.7772 | 10.069 | 0 | 0 | 0
burnt gas inlet | burnt gas | 1773.15 | 1 | 1 | 1751.0334 | 2.2761 | 5.1621 | 1321.5765 | 1117.9377 | 1306.0677 | 1014.94 | 1.2868
burnt gas outlet | burnt gas | 353.15 | 1 | 1 | 57.2228 | 0.41164 | 1.0281 | 41.1671 | -57.2751 | 1041.4177 | 750.29 | 1.388
PROCESSES | 6
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
burnt gas outlet | burnt gas outlet | burnt gas outlet | exchange | 0 | 0 | other | 0.020781
boiler | burnt gas inlet | burnt gas outlet | exchange | -35.1994 | -24.4223 | other | 0.020781
burnt gas inlet | burnt gas inlet | burnt gas inlet | exchange | 0 | 0 | other | 0.020781
heating departure | heating departure | heating departure | exchange | 0 | 0 | other | 1
heating circuit | heating return | heating departure | exchange | 35.1994 | 3.8522 | other | 1
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
boiler | -35.1994 |  | -35.1994 |  |  | -24.4223
heating circuit | 35.1994 |  | 35.1994 |  |  | 3.8522 | 20.5701
cycle | -8e-08 | 0 | -8e-08
|  |  |  | sigma(xq+) |  | 0
|  |  |  | sigma(tau+) |  | 24.4223
energy efficiency |  | 1 | exergy efficiency |  | 15.77%
|  |  | Joule effect efficiency |  | 10.94%

## evaporator sizing
| prop. glycol | propane
Cp (J/kg/K) | 3890 | 2450
mu (Pa s) | 0.005 | 0.000133
lambda (W/m/K) | 0.44 | 0.11
dh (m) | 0.02 | 0.016
Re | 20000 | 77000
Pr | 44.2045 | 2.9623
amplification factor | 1 | 5.48
Nu | 288.8941 | 288.118
h (W/m2/K) | 6355.6692 | 10854.8467
1/U |  | 0.00024946
U |  | 4008.5849
UA |  | 4200
A (m2) |  | 1.0478
20 m coaxial tube of inside diameter 16 mm and 4mm spacing
h brine 6350, h propane 10850
average h about 4000, exchange area of 1.05 m2

## CC_1P_S41
Balance
effectiveness | purchased energy | useful energy | T0 exergy
0.483 | 38134 | 18407 | 288.15
POINTS | 14
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
1 | water | 297.2495 | 0.03 | 0 | 101.0408 | 0.35452 | 0.0010027 | 101.0378 | -1.1131 | 0 | 0 | 0
2 | water | 297.4696 | 120 | 0 | 113.038 | 0.35452 | 0.0009974 | 101.0692 | 10.884 | 0 | 0 | 0
3 | water | 793.15 | 110 | 1 | 3413.7484 | 6.6092 | 0.030575 | 3077.4222 | 1509.2955 | 0 | 0 | 0
3a | water | 596.5107 | 118 | 0 | 1483.6091 | 3.4842 | 0.001519 | 1465.6852 | 479.6401 | 0 | 0 | 0
3b | water | 596.5511 | 115 | 1 | 2714.7538 | 5.5557 | 0.015396 | 2537.6954 | 1113.8902 | 0 | 0 | 0
4 | water | 297.2495 | 0.03 | 0.84972 | 2178.2985 | 7.3427 | 38.8044 | 2061.8852 | 62.5018 | 0 | 0 | 0
fuel | Montoir natural gas | 291.15 | 20 | 1 | -14.2988 | -1.1739 | 0.065739 | -11.2055 | 323.9657 | 2078.0104 | 1626.43 | 1.2777
air inlet | air | 288.15 | 1 | 1 | -9.8704 | 0.12801 | 0.8273 | -7.0424 | -46.7568 | 1001.8778 | 714.77 | 1.4017
compressed air | air | 715.7715 | 16 | 1 | 432.8431 | 0.26848 | 0.12844 | 312.8977 | 355.4811 | 1080.1978 | 793.09 | 1.362
hot gas | gaz_brulés | 1393.15 | 16 | 1 | 1258.3635 | 1.1525 | 0.25298 | 940.1716 | 926.2648 | 1258.0465 | 967.5 | 1.3003
expanded gas | gaz_brulés | 832.5928 | 1.3 | 1 | 580.7068 | 1.2619 | 1.8608 | 425.3827 | 217.0822 | 1150.6665 | 860.12 | 1.3378
gas 1 | gaz_brulés | 753.657 | 1.2 | 1 | 490.6283 | 1.1715 | 1.8248 | 358.2387 | 153.0513 | 1131.5465 | 841 | 1.3455
gas 2 | gaz_brulés | 611.2086 | 1.1 | 1 | 331.9723 | 0.96361 | 1.6144 | 240.9706 | 54.3087 | 1095.8965 | 805.35 | 1.3608
gas 3 | gaz_brulés | 447.0234 | 1 | 1 | 155.3487 | 0.65509 | 1.2988 | 112.0504 | -33.4169 | 1056.4865 | 765.94 | 1.3793
PROCESSES | 15
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
gas exhaust | gas 3 | gas 3 | exchange | 0 | 0 | other | 45.7831
HRSG 3 | gas 2 | gas 3 | exchange | -8086.3699 | -4016.3473 | other | 45.7831
HRSG 2 | gas 1 | gas 2 | exchange | -7263.7537 | -4520.7376 | other | 45.7831
HRSG 1 | expanded gas | gas 1 | exchange | -4124.0682 | -2931.5278 | other | 45.7831
air inlet | air inlet | air inlet | exchange | 0 | 0 | other | 45
fuel | fuel | fuel | exchange | 0 | 0 | other | 0.78305
feed water pump | 1 | 2 | compression | 70.7834 | 70.783 | useful | 5.9
turbine | 3 | 4 | expansion | -7289.1544 | -8536.0829 | useful | 5.9
condenser | 4 | 1 | exchange | -12255.8208 | -375.3279 | other | 5.9
economizer | 2 | 3a | exchange | 8086.3699 | 2765.6607 | other | 5.9
superheater | 3b | 3 | exchange | 4124.0682 | 2332.8911 | other | 5.9
vaporizer | 3a | 3b | exchange | 7263.7537 | 3742.0759 | other | 5.9
air compressor | air inlet | compressed air | compression | 19922.1075 | 18100.7052 | useful | 45
gas turbine | hot gas | expanded gas | expansion | -31025.1958 | -32468.5439 | useful | 45.7831
combustion chamber | compressed air | hot gas | combustion | 38133.7825 | 26410.5777 | purchased | 45.7831
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
HRSG 3 | -8.0864 |  | -8.0864 |  |  | -4.0163 | 1.2507 | 6.313%
economizer | 8.0864 |  | 8.0864 |  |  | 2.7657 |  | 0%
HRSG 2 | -7.2638 |  | -7.2638 |  |  | -4.5207 | 0.77866 | 3.93%
vaporizer | 7.2638 |  | 7.2638 |  |  | 3.7421 |  | 0%
HRSG 1 | -4.1241 |  | -4.1241 |  |  | -2.9315 | 0.59864 | 3.022%
superheater | 4.1241 |  | 4.1241 |  |  | 2.3329 |  | 0%
feed water pump | 0.070783 | 0.070783 |  |  |  | 0.070783 | 3.5038e-07 | 1.768e-06%
turbine | -7.2892 | -7.2892 |  |  |  | -8.5361 | 1.2469 | 6.294%
condenser | -12.2558 |  | -12.2558 | 288.15 |  | -0.37533 | 0.37533 | 1.894%
air compressor | 19.9221 | 19.9221 |  |  |  | 18.1007 | 1.8214 | 9.193%
gas turbine | -31.0252 | -31.0252 |  |  |  | -32.4685 | 1.4433 | 7.285%
combustion chamber | 38.1338 |  | 38.1338 |  | 38.1338 | 26.4106 | 11.7232 | 59.17%
intake / exhaust | [5 empty] | -0.57413 | 0.57413 | 2.898%
2.1041
cycle | 7.5565 | -18.3215 | 25.878 |  |  | 2.1041 | 19.8123 | 100%
|  |  |  | sigma(xq+) |  | 38.1338
|  |  |  | sigma(tau+) |  | 0
energy efficiency |  | 48.05% | exergy efficiency |  | 48.05%
Note on F56: on considère ici que l'exergie du combustible est égale à celle de son PCI
Note on H45: irréversibiltés dues à l'écart de température dans l'économiseur
Note on H47: cenerg: irréversibiltés dues à l'écart de température dans le vaporiseur
Note on H49: irréversibiltés dues à l'écart de température dans le surchauffeur
Note on H57: irreversibilties due to the release of hot gases in the atmosphere

## cogenMicroGT_S46
Bilan
efficacité | énergie payante | énergie utile | T0 exergie
0.47586 | 6355.63 | 3024.37 | 288.15
POINTS | 11
name | substance name | T (K) | P (bar) | quality | h (kJ/kg) | s (kJ/kg/K) | V (m3/kg) | u (kJ/kg) | xh (kJ/kg) | Cp | Cv | gamma
fuel | Montoir natural gas | 288.15 | 1 | 1 | -20.5207 | 0.15742 | 1.3012 | -16.0726 | -65.8799 | 2069.9404 | 1618.36 | 1.279
air inlet | air | 288.15 | 1 | 1 | -9.8704 | 0.12801 | 0.8273 | -7.0424 | -46.7568 | 1001.8778 | 714.77 | 1.4017
2 | air | 478.7598 | 5 | 1 | 183.099 | 0.17937 | 0.27491 | 131.2014 | 131.4145 | 1028.0578 | 740.95 | 1.3875
3 | burnt gas | 1223.15 | 4.5 | 1 | 1027.3831 | 1.309 | 0.78518 | 760.1347 | 650.189 | 1204.7404 | 915.87 | 1.3154
4 | burnt gas | 923.1201 | 1.2 | 1 | 673.9644 | 1.3597 | 2.2222 | 493.3857 | 282.1657 | 1148.5704 | 859.7 | 1.336
2 bis | air | 869.7969 | 4.5 | 1 | 601.8192 | 0.84639 | 0.55495 | 437.6519 | 357.9322 | 1113.5178 | 826.41 | 1.3474
5 | burnt gas | 547.8291 | 1.2 | 1 | 258.9151 | 0.78461 | 1.3188 | 186.7468 | 32.8308 | 1061.8304 | 772.96 | 1.3737
gas outlet | burnt gas | 361.5377 | 1.2 | 1 | 64.8337 | 0.35217 | 0.87031 | 46.4795 | -36.6445 | 1024.3604 | 735.49 | 1.3928
cogen inlet | water | 343.15 | 5 | 0 | 293.3863 | 0.95469 | 0.0010226 | 292.8749 | 18.2927 | 0 | 0 | 0
water cogen | water | 363.15 | 5 | 0 | 377.2997 | 1.1924 | 0.0010359 | 376.7817 | 33.7179 | 0 | 0 | 0
compressed gas | Montoir natural gas | 477.699 | 9 | 1 | 430.0246 | 0.35297 | 0.23969 | 348.876 | 328.3157 | 2713.6704 | 2262.09 | 1.1996
PROCESSES | 13
name | inlet point | outlet point | type | m ?h | m ?Xh | type_ener | flow rate
water cogen | water cogen | water cogen | exchange | 0 | 0 | other | 1820
cogen inlet | cogen inlet | cogen inlet | exchange | 0 | 0 | other | 1820
cogen water | cogen inlet | water cogen | exchange | 152722.4353 | 28073.9565 | other | 1820
cogen gas | 5 | gas outlet | exchange | -152722.4354 | -54669.9988 | useful | 786.8988
regen gas | 4 | 5 | exchange | -326601.8015 | -196201.3736 | other | 786.8988
regen air | 2 | 2 bis | exchange | 326601.8015 | 176683.7734 | other | 780
gas outlet | gas outlet | gas outlet | exchange | 0 | 0 | other | 786.8988
air inlet | air inlet | air inlet | exchange | 0 | 0 | other | 780
fuel | fuel | fuel | exchange | 0 | 0 | other | 6.8988
compressor | air inlet | 2 | compression | 150516.0719 | 138973.6248 | useful | 780
turbine | 3 | 4 | expansion | -278104.7693 | -289597.0753 | useful | 786.8988
gas compressor | fuel | compressed gas | compression | 3108.2049 | 2719.4617 | useful | 6.8988
combustion chamber | 2 bis | 3 | combustion | 339027.5412 | 232445.8406 | purchased | 786.8988
| enthalpy balance |  |  |  | exergy balance
component | dh | t | Q | Tk | dxq | dxh | dxhi | % overal losses
gas compressor | 3108.2049 | 3108.2049 |  |  |  | 0 | 3108.2049 | 1.667%
turbine | -278104.7693 | -278104.7693 |  |  |  | -289597.0753 | 11492.306 | 6.163%
regen gas | -326601.8015 |  | -326601.8015 |  |  | -196201.3736 | 19517.6001 | 10.47%
regen air | 326601.8015 |  | 326601.8015 |  |  | 176683.7734
combustion chamber | 339027.5412 |  | 339027.5412 |  | 339027.5412 | 232445.8406 | 106581.7006 | 57.16%
compressor | 150516.0719 | 150516.0719 |  |  |  | 138973.6248 | 11542.4472 | 6.19%
cogen gas | -152722.4354 |  | -152722.4354 |  |  | -54669.9988 | 26596.0423 | 14.26%
cogen water | 152722.4353 |  | 152722.4353 |  |  | 28073.9565 |  | 0%
water cogen | 0 |  | 0 |  |  | 0 |  | 0%
asp. / exhaust | [5 empty] | -7634.7911 | 7634.7911 | 4.094%
cycle | 214547.0486 | -124480.4924 | 339027.5411 |  |  | 28073.9565 | 186473.0923 | 100%
|  |  |  | sigma(xq+) |  | 339027.5412
heat-power ratio |  | 1.2269 |  | sigma(tau+) |  | 0
overall efficiency |  | 81.76%
mechanical efficiency |  | 36.72% | exergy efficiency |  | 45%
Note on F43: on considère ici que l'exergie du combustible est égale à celle de son PCI
Note on H41: irréversibiltés dues à l'écart de température dans l'échangeur
Note on H45: irréversibiltés dues à l'écart de température dans l'échangeur
Note on H46: irréversibiltés dues à l'écart de température dans l'échangeur
Note on H48: irréversibiltés dues au refoulement à l'atmosphère des gaz chauds