## macro
All worksheet on the right of worksheet "graph" will be taken into account, but you may add any number of sheets you may wish on its left, provided you do not name them "graph" or "macro", which are reserved names
The names of the worksheets will appear as the column titles in the "graph" sheet
number of lines | 9 |  | Enter here the number of values to be extracted
T air inlet | C24 |  | From line 6 to line (6 + number of lines), enter in column A the title of the value,
Pcond | D20 |  | and in column B its reference in the worksheets
Pevap | D22
Q evap | E41
m refrig | G41
UA cond | E68
UA evap | D68
tau compr | E39
eta is | J39 | Pour charger les différents fichiers de projet, opérez comme suit :
1) faites-les glisser depuis leur répertoire jusqu'à la macro : ils s'ouvrent tous comme feuilles indépendantes
2) cliquez sur le bouton "Charger les projets"
ou bien
1) faites-les glisser depuis leur répertoire jusqu'à la macro : ils s'ouvrent tous comme feuilles indépendantes
2) placez-vous successivement dans chacune des feuilles ouvertes, et utilisez la commande "Edition/Déplacer ou copier une feuille"
en choisissant comme classeur de destination celui qui contient la macro
3) si ce n'est pas déjà fait, classez les feuilles dans un ordre logique
cette seconde manière de faire est plus lente, mais vous permet de contrôler le placement des différentes feuilles
Pour extraire les informations désirées :
1) entrez colonne A, à partir de la ligne 6, les intitulés que vous souhaitez voir apparaître dans "graph"
2) entrez colonne B la référence de leur cellule dans les feuilles des différents projets
3) lorsque vous avez terminé votre sélection, entrez cellule B4 le nombre de valeurs à extraire
4) cliquez sur le bouton "extract"
Toutes les feuilles à droite de "graph" seront prises en compte, mais vous pouvez en ajouter d'autres à gauche
Load project files

## graph
| refrigAux_dP_Displ_-10_2 | refrigAux_dP_Displ_0_2 | refrigAux_dP_Displ_10_2 | refrigAux_dP_Displ_25 | refrigAux_dP_Displ_30_2
T air inlet | -10 | 0 | 10 | 25 | 30
Pcond | 3.4757 | 4.7348 | 6.3978 | 9.5976 | 10.8767
Pevap | 1.0517 | 1.0921 | 1.1361 | 1.2081 | 1.2416
Q evap | 203.83 | 188.36 | 171.07 | 140.87 | 130.97
m refrig | 1.0827 | 1.0706 | 1.0437 | 0.97922 | 0.95636
UA cond | 11.1008 | 13.763 | 14.4754 | 12.6426 | 11.8825
UA evap | 17.0301 | 16.8541 | 16.5464 | 16.9666 | 15.5441
tau compr | 61 | 46.91 | 47.75 | 53.26 | 55.15
eta is | 0.44961 | 0.71017 | 0.80397 | 0.8147 | 0.80592
| -10 | 0 | 10 | 25 | 30
compressor work (kW) | 61 | 46.91 | 47.75 | 53.26 | 55.15
cooling load (kW) | 203.83 | 188.36 | 171.07 | 140.87 | 130.97
COP | 3.3415 | 4.0153 | 3.5826 | 2.6449 | 2.3748
m refrig | 1.0827 | 1.0706 | 1.0437 | 0.97922 | 0.95636
compr ratio | 3.3049 | 4.3355 | 5.6311 | 7.9441 | 8.7602

## refrigAux_dP_Displ_-10_2
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | June 29, 2012 7:56:36 PM CEST
lang=fr | schem=simple refrigeration cycle | pilotframe=Refrig Driver Aux Charge Displacement | unit m=-
Project name | simple cycle | optimization=false | technodesign=true | thermocoupler=true
cycle de réfrigération monoétagé à compression de R134a avec surchauffe et sous-refroidissement
image=
Components | 0
PRESSURE SETTINGS | 2
name | value
HP | 4.36529
BP | 1.18779
COMPOUND GASES | 0
Gas name / Components | molar fraction | mass fraction
POINTS | 10
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
2 | R134a | 50.33352111 | 3.47568873 | 1 | 443.42318002 | 418.51136476 | 0.0716744714 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3 | R134a | -0.95888609 | 3.45092036 | 0 | 198.8265781 | 198.5610969 | 0.000769305499 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-5.1089 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
4 | R134a | -25.26368938 | 1.05166935 | 0.147604866 | 198.8265781 | 195.89023318 | 0.0279207996 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
1 | R134a | -20.74782248 | 1.03072154 | 1 | 387.08424126 | 367.22322491 | 0.192690416 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=5 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air inlet | air | -10 | 1 | 1 | -34.91176577 | -24.90605863 | 0.755524199 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air outlet | air | 0.672027577 | 1 | 1 | -24.22279288 | -17.28110819 | 0.786164424 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water inlet | prop. glycol water 40% | -10 | 1 | 0 | -36.24189011 | -36.24189011 | 0.00095342518 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water outlet | prop. glycol water 40% | -11.41068537 | 1 | 0 | -41.32846725 | -41.32846725 | 0.000952934676 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
air out fan | air | -9.90458431 | 1.00104476 | 1 | -34.81619559 | -24.83788304 | 0.75500934 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water out pump | prop. glycol water 40% | -10.00000477 | 1.09757529 | 0 | -36.23260424 | -36.23260424 | 0.000953425178 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 12
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
water outlet | water outlet | water outlet | Exchange | 0 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=water cooling | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=0.0381173873 | set molar flow=false | molar flow=1.37931034 | isobaric=false
water cooling | water out pump | water outlet | Exchange | -203.83452014 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=pump | outletStrConnected=true | outletProc=water outlet | observed=false | set volume flow=false | volume flow=0.0381370071 | set molar flow=false | molar flow=1.37931034 | isobaric=false
water inlet | water inlet | water inlet | Exchange | 0 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=pump | observed=false | set volume flow=false | volume flow=0.0381370072 | set molar flow=false | molar flow=1.37931034 | isobaric=false
air outlet | air outlet | air outlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=air cond | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=19.65411059 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air cond | air out fan | air outlet | Exchange | 264.83506777 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=fan | outletStrConnected=true | outletProc=air outlet | observed=false | set volume flow=false | volume flow=18.87523354 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air inlet | air inlet | air inlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=true | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=fan | observed=false | set volume flow=false | volume flow=0 | set molar flow=false | molar flow=0 | isobaric=false
compressor | 1 | 2 | Compression | 61 | purchased | 1.08274222 | open_syst=true | set flow=true | rend=0.44961 | isentr=true | calc_direct=true | calc_press=true | press_ratio=3.37 | cooled=false | comment= | inletStrConnected=true | inletProc=evaporator | outletStrConnected=true | outletProc=condenser | observed=true | k_polytr=1.22912 | Q_value=0
condenser | 2 | 3 | Exchange | -264.84 | other | 1.08274222 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=compressor | outletStrConnected=true | outletProc=expansion valve | observed=false | set volume flow=false | volume flow=0.0776049763 | set molar flow=false | molar flow=0.0106118946 | isobaric=false
evaporator | 4 | 1 | Exchange | 203.83 | useful | 1.08274222 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=expansion valve | outletStrConnected=true | outletProc=compressor | observed=false | set volume flow=false | volume flow=0.0302310285 | set molar flow=false | molar flow=0.0106118946 | isobaric=false
expansion valve | 3 | 4 | Throttle | 0 | other | 1.08274222 | open_syst=true | set flow=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=evaporator | observed=false
fan | air inlet | air out fan | Compression | 2.39 | purchased | 25 | open_syst=true | set flow=false | rend=0.8 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1 | cooled=false | comment= | inletStrConnected=true | inletProc=air inlet | outletStrConnected=true | outletProc=air cond | observed=false | k_polytr=1.5318 | Q_value=0
pump | water inlet | water out pump | Compression | 0.371 | purchased | 40 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1.1 | cooled=false | comment= | inletStrConnected=true | inletProc=water inlet | outletStrConnected=true | outletProc=water cooling | observed=false | k_polytr=53096784.60131001 | Q_value=0
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | air cond | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.851494363 | CalcDim=false | set design=true | UA=11.14904966 | DTmin=7.366
evaporator | water cooling | evaporator | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.295856932 | CalcDim=false | set design=true | UA=16.66021578 | DTmin=12.177
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=evaporator | compType=HeatEx | ADesign_value=18.19990 | eLambda=0
type=ext_tube | free_flow=0.08 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.272912 | dPSing=0 | C1=0.33 | a_Re=0.6 | b_Pr=0.33 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=0.02 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.045444 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=24.99992 | eLambda=0
type=cond | free_flow=0.005 | Dh=0.02 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.025642 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=air_coil | free_flow=1 | Dh=0.01 | length=0.15 | surf_fact=20 | fin=0.4 | pres_aval=false | DPArea=0.029521 | dPSing=0 | C1=1.0 | a_Re=0.77 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=compressor | compType=Compression | alpha_value=0.038 | a0_value=0.96 | K1_value=0.5 | K2_value=4.48 | K3_value=-15.68 | R1_value=0 | R2_value=0 | N_value=1500.0141 | Vs_value=0.01003201 | KnonAdiab=0 | Device_number=1
PILOT
mCpRefrigEvap=40.76690385282528 | mCpRefrigCond=5.173918747932041 | N_value=1500.0141 | UAevap=17.03009596807641 | UAcond=11.100849775664242 | mCpCalopEvap=144.55777420045098 | mCpCalopCond=25.04674262351326 | DeltaHevap=203.83451926412638 | DeltaHcond=264.83506688909404 | tauCompr=61.00054762496764 | AdesignEvap=18.2000 | AdesignCond=25.0000 | lineLength=0.5000 | #technoEvap=3steps=false:ADesign_value=18.19990:@confHot=type=ext_tube:free_flow=0.08:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.272912:C1=0.33:a_Re=0.6:b_Pr=0.33:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=0.02:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.045444:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=24.99992:@confHot=type=cond:free_flow=0.005:Dh=0.02:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.025642:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=air_coil:free_flow=1:Dh=0.01:length=0.15:surf_fact=20:fin=0.4:pres_aval=false:DPArea=0.029521:C1=1.0:a_Re=0.77:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#

## refrigAux_dP_Displ_0_2
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | June 29, 2012 7:55:37 PM CEST
lang=fr | schem=simple refrigeration cycle | pilotframe=Refrig Driver Aux Charge Displacement | unit m=-
Project name | simple cycle | optimization=false | technodesign=true | thermocoupler=true
cycle de réfrigération monoétagé à compression de R134a avec surchauffe et sous-refroidissement
image=
Components | 0
PRESSURE SETTINGS | 2
name | value
HP | 4.36529
BP | 1.18779
COMPOUND GASES | 0
Gas name / Components | molar fraction | mass fraction
POINTS | 10
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
2 | R134a | 39.70401379 | 4.73484894 | 1 | 431.4597532 | 408.13959097 | 0.0492521779 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3 | R134a | 8.54643139 | 4.7164917 | 0 | 211.71447741 | 211.34234914 | 0.000788993806 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-5.1089 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
4 | R134a | -24.42903065 | 1.09210631 | 0.202759707 | 211.71447741 | 207.69820687 | 0.036775454 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
1 | R134a | -19.86931811 | 1.07268186 | 1 | 387.64513135 | 367.73705814 | 0.185591591 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=5 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air inlet | air | 0 | 1 | 1 | -24.89588868 | -17.76125963 | 0.78423498 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air outlet | air | 9.51051947 | 1 | 1 | -15.36973314 | -10.96564849 | 0.811540424 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water inlet | prop. glycol water 40% | -10 | 1 | 0 | -36.24189011 | -36.24189011 | 0.00095342518 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water outlet | prop. glycol water 40% | -11.30333025 | 1 | 0 | -40.94159777 | -40.94159777 | 0.000952971717 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
air out fan | air | 0.115218735 | 1.00109115 | 1 | -24.78048701 | -17.67893816 | 0.78371064 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water out pump | prop. glycol water 40% | -10.00000477 | 1.09738293 | 0 | -36.23262258 | -36.23262258 | 0.000953425178 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 12
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
water outlet | water outlet | water outlet | Exchange | 0 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=water cooling | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=0.0381188687 | set molar flow=false | molar flow=1.37931034 | isobaric=false
water cooling | water out pump | water outlet | Exchange | -188.35900758 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=pump | outletStrConnected=true | outletProc=water outlet | observed=false | set volume flow=false | volume flow=0.0381370071 | set molar flow=false | molar flow=1.37931034 | isobaric=false
water inlet | water inlet | water inlet | Exchange | 0 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=pump | observed=false | set volume flow=false | volume flow=0.0381370072 | set molar flow=false | molar flow=1.37931034 | isobaric=false
air outlet | air outlet | air outlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=air cond | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=20.2885106 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air cond | air out fan | air outlet | Exchange | 235.26884679 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=fan | outletStrConnected=true | outletProc=air outlet | observed=false | set volume flow=false | volume flow=19.5927659 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air inlet | air inlet | air inlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=true | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=fan | observed=false | set volume flow=false | volume flow=0 | set molar flow=false | molar flow=0 | isobaric=false
compressor | 1 | 2 | Compression | 46.91 | purchased | 1.07064348 | open_syst=true | set flow=true | rend=0.71017 | isentr=true | calc_direct=true | calc_press=true | press_ratio=4.41 | cooled=false | comment= | inletStrConnected=true | inletProc=evaporator | outletStrConnected=true | outletProc=condenser | observed=true | k_polytr=1.11925 | Q_value=0
condenser | 2 | 3 | Exchange | -235.27 | other | 1.07064348 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=compressor | outletStrConnected=true | outletProc=expansion valve | observed=false | set volume flow=false | volume flow=0.0527315231 | set molar flow=false | molar flow=0.0104933156 | isobaric=false
evaporator | 4 | 1 | Exchange | 188.36 | useful | 1.07064348 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=expansion valve | outletStrConnected=true | outletProc=compressor | observed=false | set volume flow=false | volume flow=0.0393734001 | set molar flow=false | molar flow=0.0104933156 | isobaric=false
expansion valve | 3 | 4 | Throttle | 0 | other | 1.07064348 | open_syst=true | set flow=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=evaporator | observed=false
fan | air inlet | air out fan | Compression | 2.89 | purchased | 25 | open_syst=true | set flow=false | rend=0.8 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1 | cooled=false | comment= | inletStrConnected=true | inletProc=air inlet | outletStrConnected=true | outletProc=air cond | observed=false | k_polytr=1.63055 | Q_value=0
pump | water inlet | water out pump | Compression | 0.371 | purchased | 40 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1.1 | cooled=false | comment= | inletStrConnected=true | inletProc=water inlet | outletStrConnected=true | outletProc=water cooling | observed=false | k_polytr=52996825.43368001 | Q_value=0
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | air cond | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.787030329 | CalcDim=false | set design=true | UA=13.79125351 | DTmin=7.366
evaporator | water cooling | evaporator | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.316009727 | CalcDim=false | set design=true | UA=16.4934458 | DTmin=12.177
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=evaporator | compType=HeatEx | ADesign_value=18.20002 | eLambda=0
type=ext_tube | free_flow=0.08 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.272374 | dPSing=0 | C1=0.33 | a_Re=0.6 | b_Pr=0.33 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=0.02 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.045477 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=24.99998 | eLambda=0
type=cond | free_flow=0.005 | Dh=0.02 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.025373 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=air_coil | free_flow=1 | Dh=0.01 | length=0.15 | surf_fact=20 | fin=0.4 | pres_aval=false | DPArea=0.029702 | dPSing=0 | C1=1.0 | a_Re=0.77 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=compressor | compType=Compression | alpha_value=0.038 | a0_value=0.96 | K1_value=0.5 | K2_value=4.48 | K3_value=-15.68 | R1_value=0 | R2_value=0 | N_value=1500.0141 | Vs_value=0.01003201 | KnonAdiab=0 | Device_number=1
PILOT
mCpRefrigEvap=37.671801669413476 | mCpRefrigCond=7.561293328207939 | N_value=1500.0141 | UAevap=16.85406741476777 | UAcond=13.763023325561228 | mCpCalopEvap=144.55777420045098 | mCpCalopCond=25.04674262351326 | DeltaHevap=188.35900834706737 | DeltaHcond=235.2688475652439 | tauCompr=46.90983921817652 | AdesignEvap=18.2000 | AdesignCond=25.0000 | lineLength=0.5000 | #technoEvap=3steps=false:ADesign_value=18.20002:@confHot=type=ext_tube:free_flow=0.08:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.272374:C1=0.33:a_Re=0.6:b_Pr=0.33:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=0.02:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.045477:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=24.99998:@confHot=type=cond:free_flow=0.005:Dh=0.02:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.025373:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=air_coil:free_flow=1:Dh=0.01:length=0.15:surf_fact=20:fin=0.4:pres_aval=false:DPArea=0.029702:C1=1.0:a_Re=0.77:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#

## refrigAux_dP_Displ_10_2
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | June 29, 2012 7:53:15 PM CEST
lang=fr | schem=simple refrigeration cycle | pilotframe=Refrig Driver Aux Charge Displacement | unit m=-
Project name | simple cycle | optimization=false | technodesign=true | thermocoupler=true
cycle de réfrigération monoétagé à compression de R134a avec surchauffe et sous-refroidissement
image=
Components | 0
PRESSURE SETTINGS | 2
name | value
HP | 4.36529
BP | 1.18779
COMPOUND GASES | 0
Gas name / Components | molar fraction | mass fraction
POINTS | 10
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
2 | R134a | 45.55921488 | 6.39776 | 1 | 433.99088121 | 410.8909416 | 0.0361062929 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3 | R134a | 17.59805838 | 6.38457115 | 0 | 224.32688417 | 223.80990625 | 0.000809730073 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-5.1089 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
4 | R134a | -23.54759919 | 1.13614156 | 0.256673075 | 224.32688417 | 219.24971382 | 0.0446878324 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
1 | R134a | -18.94001288 | 1.11851716 | 1 | 388.23793812 | 368.28075849 | 0.178425333 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=5 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air inlet | air | 10 | 1 | 1 | -14.87940406 | -10.6158531 | 0.812945761 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air outlet | air | 18.84891413 | 1 | 1 | -6.01395954 | -4.29100092 | 0.838351684 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water inlet | prop. glycol water 40% | -10 | 1 | 0 | -36.24189011 | -36.24189011 | 0.00095342518 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water outlet | prop. glycol water 40% | -11.18343335 | 1 | 0 | -40.50948815 | -40.50948815 | 0.000953013141 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
air out fan | air | 10.11220512 | 1.0011377 | 1 | -14.76700361 | -10.53566762 | 0.812343708 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water out pump | prop. glycol water 40% | -10.00000477 | 1.09716759 | 0 | -36.23264311 | -36.23264311 | 0.000953425178 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 12
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
water outlet | water outlet | water outlet | Exchange | 0 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=water cooling | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=0.0381205257 | set molar flow=false | molar flow=1.37931034 | isobaric=false
water cooling | water out pump | water outlet | Exchange | -171.07380145 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=pump | outletStrConnected=true | outletProc=water outlet | observed=false | set volume flow=false | volume flow=0.0381370071 | set molar flow=false | molar flow=1.37931034 | isobaric=false
water inlet | water inlet | water inlet | Exchange | 0 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=pump | observed=false | set volume flow=false | volume flow=0.0381370072 | set molar flow=false | molar flow=1.37931034 | isobaric=false
air outlet | air outlet | air outlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=air cond | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=20.95879211 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air cond | air out fan | air outlet | Exchange | 218.82610195 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=fan | outletStrConnected=true | outletProc=air outlet | observed=false | set volume flow=false | volume flow=20.30859268 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air inlet | air inlet | air inlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=true | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=fan | observed=false | set volume flow=false | volume flow=0 | set molar flow=false | molar flow=0 | isobaric=false
compressor | 1 | 2 | Compression | 47.75 | purchased | 1.04369899 | open_syst=true | set flow=true | rend=0.80397 | isentr=true | calc_direct=true | calc_press=true | press_ratio=5.72 | cooled=false | comment= | inletStrConnected=true | inletProc=evaporator | outletStrConnected=true | outletProc=condenser | observed=true | k_polytr=1.09153 | Q_value=0
condenser | 2 | 3 | Exchange | -218.83 | other | 1.04369899 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=compressor | outletStrConnected=true | outletProc=expansion valve | observed=false | set volume flow=false | volume flow=0.0376841014 | set molar flow=false | molar flow=0.0102292342 | isobaric=false
evaporator | 4 | 1 | Exchange | 171.07 | useful | 1.04369899 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=expansion valve | outletStrConnected=true | outletProc=compressor | observed=false | set volume flow=false | volume flow=0.0466406455 | set molar flow=false | molar flow=0.0102292342 | isobaric=false
expansion valve | 3 | 4 | Throttle | 0 | other | 1.04369899 | open_syst=true | set flow=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=evaporator | observed=false
fan | air inlet | air out fan | Compression | 2.81 | purchased | 25 | open_syst=true | set flow=false | rend=0.8 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1 | cooled=false | comment= | inletStrConnected=true | inletProc=air inlet | outletStrConnected=true | outletProc=air cond | observed=false | k_polytr=1.53478 | Q_value=0
pump | water inlet | water out pump | Compression | 0.37 | purchased | 40 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1.1 | cooled=false | comment= | inletStrConnected=true | inletProc=water inlet | outletStrConnected=true | outletProc=water cooling | observed=false | k_polytr=52884903.18568001 | Q_value=0
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | air cond | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.788815663 | CalcDim=false | set design=true | UA=14.4791835 | DTmin=7.366
evaporator | water cooling | evaporator | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.34010365 | CalcDim=false | set design=true | UA=16.20059926 | DTmin=12.177
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=evaporator | compType=HeatEx | ADesign_value=18.19900 | eLambda=0
type=ext_tube | free_flow=0.08 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.271772 | dPSing=0 | C1=0.33 | a_Re=0.6 | b_Pr=0.33 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=0.02 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.045710 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=25.00015 | eLambda=0
type=cond | free_flow=0.005 | Dh=0.02 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.025176 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=air_coil | free_flow=1 | Dh=0.01 | length=0.15 | surf_fact=20 | fin=0.4 | pres_aval=false | DPArea=0.029878 | dPSing=0 | C1=1.0 | a_Re=0.77 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=compressor | compType=Compression | alpha_value=0.038 | a0_value=0.96 | K1_value=0.5 | K2_value=4.48 | K3_value=-15.68 | R1_value=0 | R2_value=0 | N_value=1499.6541 | Vs_value=0.01003201 | KnonAdiab=0 | Device_number=1
PILOT
mCpRefrigEvap=34.21476037399553 | mCpRefrigCond=7.826612532320939 | N_value=1499.6541 | UAevap=16.546371235645257 | UAcond=14.475398800365731 | mCpCalopEvap=144.66981629659134 | mCpCalopCond=25.069575902759713 | DeltaHevap=171.07380186997764 | DeltaHcond=218.82610236758984 | tauCompr=47.75230049761218 | AdesignEvap=18.2000 | AdesignCond=25.0000 | lineLength=0.5000 | #technoEvap=3steps=false:ADesign_value=18.19900:@confHot=type=ext_tube:free_flow=0.08:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.271772:C1=0.33:a_Re=0.6:b_Pr=0.33:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=0.02:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.045710:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=25.00015:@confHot=type=cond:free_flow=0.005:Dh=0.02:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.025176:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=air_coil:free_flow=1:Dh=0.01:length=0.15:surf_fact=20:fin=0.4:pres_aval=false:DPArea=0.029878:C1=1.0:a_Re=0.77:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#

## refrigAux_dP_Displ_25
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | July 2, 2012 11:59:43 AM CEST
lang=fr | schem=simple refrigeration cycle | pilotframe=Refrig Driver Aux Charge Displacement | unit m=-
Project name | simple cycle | optimization=false | technodesign=true | thermocoupler=true
cycle de réfrigération monoétagé à compression de R134a avec surchauffe et sous-refroidissement
image=
Components | 0
PRESSURE SETTINGS | 2
name | value
HP | 4.36529
BP | 1.18779
COMPOUND GASES | 0
Gas name / Components | molar fraction | mass fraction
POINTS | 10
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
2 | R134a | 60.76352198 | 9.59755399 | 1 | 443.57345978 | 420.32651457 | 0.0242217395 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3 | R134a | 32.44441264 | 9.58975687 | 0 | 245.32064466 | 244.50636868 | 0.000849110142 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-5.1089 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
4 | R134a | -22.16289676 | 1.20812861 | 0.347473227 | 245.32064466 | 238.4488478 | 0.0568796798 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
1 | R134a | -17.4610004 | 1.19461981 | 1 | 389.18023787 | 369.14635325 | 0.167700925 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=5 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air inlet | air | 25 | 1 | 1 | 0.150342748 | 0.107276576 | 0.856011932 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air outlet | air | 32.87649573 | 1 | 1 | 8.04650322 | 5.74203362 | 0.878625966 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water inlet | prop. glycol water 40% | -10 | 1 | 0 | -36.24189011 | -36.24189011 | 0.00095342518 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water outlet | prop. glycol water 40% | -12.60496925 | 1 | 0 | -45.62972733 | -45.62972733 | 0.000952525791 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
air out fan | air | 25.13050137 | 1.00120804 | 1 | 0.281143199 | 0.200609067 | 0.855353307 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water out pump | prop. glycol water 40% | -10.00000477 | 1.03742886 | 0 | -36.23833875 | -36.23833875 | 0.000953425178 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 12
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
water outlet | water outlet | water outlet | Exchange | 0 | other | 15 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=water cooling | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=0.0142878895 | set molar flow=false | molar flow=0.517241379 | isobaric=false
water cooling | water out pump | water outlet | Exchange | -140.8708286 | other | 15 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=pump | outletStrConnected=true | outletProc=water outlet | observed=false | set volume flow=false | volume flow=0.0143013777 | set molar flow=false | molar flow=0.517241379 | isobaric=false
water inlet | water inlet | water inlet | Exchange | 0 | other | 15 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=pump | observed=false | set volume flow=false | volume flow=0.0143013777 | set molar flow=false | molar flow=0.517241379 | isobaric=false
air outlet | air outlet | air outlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=air cond | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=21.96564916 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air cond | air out fan | air outlet | Exchange | 194.13400048 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=fan | outletStrConnected=true | outletProc=air outlet | observed=false | set volume flow=false | volume flow=21.38383277 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air inlet | air inlet | air inlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=true | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=fan | observed=false | set volume flow=false | volume flow=0 | set molar flow=false | molar flow=0 | isobaric=false
compressor | 1 | 2 | Compression | 53.26 | purchased | 0.979224433 | open_syst=true | set flow=true | rend=0.8147 | isentr=true | calc_direct=true | calc_press=true | press_ratio=8.03 | cooled=false | comment= | inletStrConnected=true | inletProc=evaporator | outletStrConnected=true | outletProc=condenser | observed=true | k_polytr=1.07688 | Q_value=0
condenser | 2 | 3 | Exchange | -194.13 | other | 0.979224433 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=compressor | outletStrConnected=true | outletProc=expansion valve | observed=false | set volume flow=false | volume flow=0.0237185191 | set molar flow=false | molar flow=0.00959732271 | isobaric=false
evaporator | 4 | 1 | Exchange | 140.87 | useful | 0.979224433 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=expansion valve | outletStrConnected=true | outletProc=compressor | observed=false | set volume flow=false | volume flow=0.0556979722 | set molar flow=false | molar flow=0.00959732271 | isobaric=false
expansion valve | 3 | 4 | Throttle | 0 | other | 0.979224433 | open_syst=true | set flow=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=evaporator | observed=false
fan | air inlet | air out fan | Compression | 3.27 | purchased | 25 | open_syst=true | set flow=false | rend=0.8 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1 | cooled=false | comment= | inletStrConnected=true | inletProc=air inlet | outletStrConnected=true | outletProc=air cond | observed=false | k_polytr=1.56854 | Q_value=0
pump | water inlet | water out pump | Compression | 0.0533 | purchased | 15 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1.04 | cooled=false | comment= | inletStrConnected=true | inletProc=water inlet | outletStrConnected=true | outletProc=water cooling | observed=false | k_polytr=20955852.26321 | Q_value=0
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | air cond | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.794743439 | CalcDim=false | set design=true | UA=12.62938163 | DTmin=7.366
evaporator | water cooling | evaporator | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.38657717 | CalcDim=false | set design=true | UA=16.63915537 | DTmin=12.177
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=evaporator | compType=HeatEx | ADesign_value=24.99876 | eLambda=0
type=ext_tube | free_flow=0.08 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.744442 | dPSing=0 | C1=0.33 | a_Re=0.6 | b_Pr=0.33 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=0.02 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.046434 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=24.99994 | eLambda=0
type=cond | free_flow=0.005 | Dh=0.02 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.025032 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=air_coil | free_flow=1 | Dh=0.01 | length=0.15 | surf_fact=20 | fin=0.4 | pres_aval=false | DPArea=0.030130 | dPSing=0 | C1=1.0 | a_Re=0.77 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=compressor | compType=Compression | alpha_value=0.038 | a0_value=0.96 | K1_value=0.5 | K2_value=4.48 | K3_value=-15.68 | R1_value=0 | R2_value=0 | N_value=1500.0560 | Vs_value=0.01003201 | KnonAdiab=0 | Device_number=1
PILOT
mCpRefrigEvap=28.17416570625184 | mCpRefrigCond=6.850261370052311 | N_value=1500.056 | UAevap=16.966557233729326 | UAcond=12.642570209045562 | mCpCalopEvap=54.083809627734915 | mCpCalopCond=25.069570318970264 | DeltaHevap=140.8708285312592 | DeltaHcond=194.1340004226778 | tauCompr=53.26317189141857 | AdesignEvap=25.0000 | AdesignCond=25.0000 | lineLength=0.5000 | #technoEvap=3steps=false:ADesign_value=24.99876:@confHot=type=ext_tube:free_flow=0.08:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.744442:C1=0.33:a_Re=0.6:b_Pr=0.33:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=0.02:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.046434:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=24.99994:@confHot=type=cond:free_flow=0.005:Dh=0.02:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.025032:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=air_coil:free_flow=1:Dh=0.01:length=0.15:surf_fact=20:fin=0.4:pres_aval=false:DPArea=0.030130:C1=1.0:a_Re=0.77:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#

## refrigAux_dP_Displ_30_2
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | June 29, 2012 7:51:22 PM CEST
lang=fr | schem=simple refrigeration cycle | pilotframe=Refrig Driver Aux Charge Displacement | unit m=-
Project name | simple cycle | optimization=false | technodesign=true | thermocoupler=true
cycle de réfrigération monoétagé à compression de R134a avec surchauffe et sous-refroidissement
image=
Components | 0
PRESSURE SETTINGS | 2
name | value
HP | 4.36529
BP | 1.18779
COMPOUND GASES | 0
Gas name / Components | molar fraction | mass fraction
POINTS | 10
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
2 | R134a | 66.3691562 | 10.87670591 | 1 | 447.24299756 | 423.9246944 | 0.0214387549 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3 | R134a | 37.44106998 | 10.87017702 | 0 | 252.62519751 | 251.68579711 | 0.000864199726 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-5.1089 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
4 | R134a | -21.54072819 | 1.24160476 | 0.378569084 | 252.62519751 | 245.13307377 | 0.0603422601 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
1 | R134a | -16.83730787 | 1.22790206 | 1 | 389.5771474 | 369.51145874 | 0.163414406 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=5 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air inlet | air | 30 | 1 | 1 | 5.16242779 | 3.68382258 | 0.870367323 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=true
air outlet | air | 37.55329564 | 1 | 1 | 12.73671517 | 9.08949979 | 0.892053424 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water inlet | prop. glycol water 40% | -10 | 1 | 0 | -36.24189011 | -36.24189011 | 0.00095342518 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water outlet | prop. glycol water 40% | -10.90534182 | 1 | 0 | -39.5070647 | -39.5070647 | 0.000953109449 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
air out fan | air | 30.12899456 | 1.00123158 | 1 | 5.29175199 | 3.77611143 | 0.869666608 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
water out pump | prop. glycol water 40% | -10.00000477 | 1.09666445 | 0 | -36.23269108 | -36.23269108 | 0.000953425178 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 12
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
water outlet | water outlet | water outlet | Exchange | 0 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=water cooling | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=0.0381244045 | set molar flow=false | molar flow=1.37931034 | isobaric=false
water cooling | water out pump | water outlet | Exchange | -130.97494471 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=pump | outletStrConnected=true | outletProc=water outlet | observed=false | set volume flow=false | volume flow=0.0381370071 | set molar flow=false | molar flow=1.37931034 | isobaric=false
water inlet | water inlet | water inlet | Exchange | 0 | other | 40 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=pump | observed=false | set volume flow=false | volume flow=0.0381370072 | set molar flow=false | molar flow=1.37931034 | isobaric=false
air outlet | air outlet | air outlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=air cond | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=22.30133561 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air cond | air out fan | air outlet | Exchange | 186.12407945 | other | 25 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=fan | outletStrConnected=true | outletProc=air outlet | observed=false | set volume flow=false | volume flow=21.7416653 | set molar flow=false | molar flow=0.863326344 | isobaric=false
air inlet | air inlet | air inlet | Exchange | 0 | other | 25 | open_syst=true | set flow=false | calc_direct=true | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=fan | observed=false | set volume flow=false | volume flow=0 | set molar flow=false | molar flow=0 | isobaric=false
compressor | 1 | 2 | Compression | 55.15 | purchased | 0.956356918 | open_syst=true | set flow=true | rend=0.80592 | isentr=true | calc_direct=true | calc_press=true | press_ratio=8.86 | cooled=false | comment= | inletStrConnected=true | inletProc=evaporator | outletStrConnected=true | outletProc=condenser | observed=true | k_polytr=1.07396 | Q_value=0
condenser | 2 | 3 | Exchange | -186.12 | other | 0.956356918 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=compressor | outletStrConnected=true | outletProc=expansion valve | observed=false | set volume flow=false | volume flow=0.0205031015 | set molar flow=false | molar flow=0.0093731995 | isobaric=false
evaporator | 4 | 1 | Exchange | 130.97 | useful | 0.956356918 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=expansion valve | outletStrConnected=true | outletProc=compressor | observed=false | set volume flow=false | volume flow=0.0577087379 | set molar flow=false | molar flow=0.0093731995 | isobaric=false
expansion valve | 3 | 4 | Throttle | 0 | other | 0.956356918 | open_syst=true | set flow=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=evaporator | observed=false
fan | air inlet | air out fan | Compression | 3.23 | purchased | 25 | open_syst=true | set flow=false | rend=0.8 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1 | cooled=false | comment= | inletStrConnected=true | inletProc=air inlet | outletStrConnected=true | outletProc=air cond | observed=false | k_polytr=1.52821 | Q_value=0
pump | water inlet | water out pump | Compression | 0.368 | purchased | 40 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=1.1 | cooled=false | comment= | inletStrConnected=true | inletProc=water inlet | outletStrConnected=true | outletProc=water cooling | observed=false | k_polytr=52623314.88911001 | Q_value=0
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | air cond | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.798232814 | CalcDim=false | set design=true | UA=11.87001906 | DTmin=7.366
evaporator | water cooling | evaporator | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.407549869 | CalcDim=false | set design=true | UA=15.23501805 | DTmin=12.177
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=evaporator | compType=HeatEx | ADesign_value=18.20784 | eLambda=0
type=ext_tube | free_flow=0.08 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.270373 | dPSing=0 | C1=0.33 | a_Re=0.6 | b_Pr=0.33 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=0.02 | Dh=0.01 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.046690 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=25.00059 | eLambda=0
type=cond | free_flow=0.005 | Dh=0.02 | length=3 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.025003 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=air_coil | free_flow=1 | Dh=0.01 | length=0.15 | surf_fact=20 | fin=0.4 | pres_aval=false | DPArea=0.030212 | dPSing=0 | C1=1.0 | a_Re=0.77 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=compressor | compType=Compression | alpha_value=0.038 | a0_value=0.96 | K1_value=0.5 | K2_value=4.48 | K3_value=-15.68 | R1_value=0 | R2_value=0 | N_value=1500.0560 | Vs_value=0.01003201 | KnonAdiab=0 | Device_number=1
PILOT
mCpRefrigEvap=26.194988931676466 | mCpRefrigCond=6.429627725650281 | N_value=1500.056 | UAevap=15.54405965008751 | UAcond=11.88245875423238 | mCpCalopEvap=144.419539222572 | mCpCalopCond=25.06957031978717 | DeltaHevap=130.97494465838233 | DeltaHcond=186.1240793996685 | tauCompr=55.149134741286154 | AdesignEvap=18.2000 | AdesignCond=25.0000 | lineLength=0.5000 | #technoEvap=3steps=false:ADesign_value=18.20784:@confHot=type=ext_tube:free_flow=0.08:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.270373:C1=0.33:a_Re=0.6:b_Pr=0.33:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=0.02:Dh=0.01:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.046690:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=25.00059:@confHot=type=cond:free_flow=0.005:Dh=0.02:length=3:surf_fact=1:fin=1:pres_aval=false:DPArea=0.025003:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=air_coil:free_flow=1:Dh=0.01:length=0.15:surf_fact=20:fin=0.4:pres_aval=false:DPArea=0.030212:C1=1.0:a_Re=0.77:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#