## macro
All worksheet on the right of worksheet "graph" will be taken into account, but you may add any number of sheets you may wish on its left, provided you do not name them "graph" or "macro", which are reserved names
The names of the worksheets will appear as the column titles in the "graph" sheet
number of lines | 6 |  | Enter here the number of values to be extracted
tau HP turb | E43 |  | From line 6 to line (6 + number of lines), enter in column A the title of the value,
Q boiler | E45 |  | and in column B its reference in the worksheets
T water | C31
P cond | D25
UA cond | E69
m (kg/s) | G43
Pour charger les différents fichiers de projet, opérez comme suit :
1) faites-les glisser depuis leur répertoire jusqu'à la macro : ils s'ouvrent tous comme feuilles indépendantes
2) cliquez sur le bouton "Charger les projets"
ou bien
1) faites-les glisser depuis leur répertoire jusqu'à la macro : ils s'ouvrent tous comme feuilles indépendantes
2) placez-vous successivement dans chacune des feuilles ouvertes, et utilisez la commande "Edition/Déplacer ou copier une feuille"
en choisissant comme classeur de destination celui qui contient la macro
3) si ce n'est pas déjà fait, classez les feuilles dans un ordre logique
cette seconde manière de faire est plus lente, mais vous permet de contrôler le placement des différentes feuilles
Pour extraire les informations désirées :
1) entrez colonne A, à partir de la ligne 6, les intitulés que vous souhaitez voir apparaître dans "graph"
2) entrez colonne B la référence de leur cellule dans les feuilles des différents projets
3) lorsque vous avez terminé votre sélection, entrez cellule B4 le nombre de valeurs à extraire
4) cliquez sur le bouton "extract"
Toutes les feuilles à droite de "graph" seront prises en compte, mais vous pouvez en ajouter d'autres à gauche
Load project files

## graph
| steamOffDesign_4 | steamOffDesign_8 | steamOffDesign_12 | steamOffDesign_16 | steamOffDesign_20 | steamOffDesign_24
tau HP turb | -680138.6 | -671415.24 | -662911.54 | -654671.37 | -646734.84 | -639145.61
Q boiler | 1725918.27 | 1718082.8 | 1710194.37 | 1702257.87 | 1694278.32 | 1686260.26
T water | 4 | 8 | 12 | 16 | 20 | 24
P cond | 0.027942 | 0.034749 | 0.04302 | 0.053019 | 0.065043 | 0.079428
UA cond | 102979.888 | 107369.9698 | 111874.2224 | 116360.202 | 121097.0345 | 125621.3369
m (kg/s) | 512.9388 | 512.9388 | 512.9388 | 512.9388 | 512.9387 | 512.9387
| 4 | 8 | 12 | 16 | 20 | 24
mechanical power (kW) | 680138.6 | 671415.24 | 662911.54 | 654671.37 | 646734.84 | 639145.61
P cond (bar) | 0.027942 | 0.034749 | 0.04302 | 0.053019 | 0.065043 | 0.079428
UA cond (kW) | 102979.888 | 107369.9698 | 111874.2224 | 116360.202 | 121097.0345 | 125621.3369
cycle efficiency | 0.39407 | 0.39079 | 0.38762 | 0.38459 | 0.38172 | 0.37903

## steamOffDesign_4
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | July 1, 2012 9:44:18 PM CEST
lang=fr | schem=steam power plant | pilotframe=Steam plant driver | unit m=kg/s
Project name | Simple steam plant | optimization=false | technodesign=true | thermocoupler=true
steam power plant
image=
Components | 0
PRESSURE SETTINGS | 0
name | value
COMPOUND GASES | 1
Gas name / Components | molar fraction | mass fraction
burnt gases | 5
CO2 | 0.0421611297 | 0.0652103215
H2O | 0.0811099829 | 0.0513534983
O2 | 0.119000221 | 0.133824666
N2 | 0.749100889 | 0.737497993
Ar | 0.00862777745 | 0.0121135218
POINTS | 8
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
1 | water | 21.92074 | 0.0279422216 | 0 | 91.93239436 | 91.92959415 | 0.00100214202 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-1 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
2 | water | 22.19973135 | 165 | 0 | 108.40465875 | 91.98879932 | 0.000994900571 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3b | water | 565 | 165 | 1 | 3473.16909837 | 3123.98520995 | 0.0211626599 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
4 | water | 22.92074 | 0.0279422216 | 0.838059694 | 2147.20471627 | 2032.83605121 | 40.9304123 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0.0000000226622 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
hot gas | burnt gases | 1597.28445112 | 1 | 1 | 1905.75859072 | 1446.30962512 | 5.46521461 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
cooled gas | burnt gases | 1047.45207295 | 1 | 1 | 1186.62597509 | 887.83230245 | 3.85866168 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river inlet | water | 4 | 3 | 0 | 17.14408034 | 16.84411422 | 0.000999887057 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river outlet | water | 17.97494 | 3 | 0 | 75.71235474 | 75.41199714 | 0.001001192 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 10
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
river outlet | river outlet | river outlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=river | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=18.02145603 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river | river inlet | river outlet | Exchange | 1054228.93915596 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=river inlet | outletStrConnected=true | outletProc=river outlet | observed=false | set volume flow=false | volume flow=17.99796702 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river inlet | river inlet | river inlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=river | observed=false | set volume flow=false | volume flow=18.02860078 | set molar flow=false | molar flow=999.15183111 | isobaric=true
cooled gas | cooled gas | cooled gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=boiler | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=9259.77539463 | set molar flow=false | molar flow=84.3462831 | isobaric=true
boiler | hot gas | cooled gas | Exchange | -1725918.27750311 | purchased | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=hot gas | outletStrConnected=true | outletProc=cooled gas | observed=false | set volume flow=false | volume flow=13116.51506747 | set molar flow=false | molar flow=84.3462831 | isobaric=true
hot gas | hot gas | hot gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=boiler | observed=false | set volume flow=false | volume flow=12812.38795086 | set molar flow=false | molar flow=84.3462831 | isobaric=true
feedwater pump | 1 | 2 | Compression | 8449.26 | useful | 512.93881006 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=5905.04 | cooled=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=vaporizer | observed=false | k_polytr=1197.36821 | Q_value=0
turbine | 3b | 4 | Expansion | -680138.6 | useful | 512.93881006 | open_syst=true | set flow=true | rend=0.85593 | isentr=true | calc_direct=true | calc_press=true | press_ratio=5905.04 | cooled=false | comment= | inletStrConnected=true | inletProc=vaporizer | outletStrConnected=true | outletProc=condenser | observed=false | k_polytr=1.1475 | Q_value=0 | mechBalanced=false | mechBalancedCompr=
condenser | 4 | 1 | Exchange | -1054228.94 | other | 512.93881006 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=turbine | outletStrConnected=true | outletProc=feedwater pump | observed=false | set volume flow=false | volume flow=20994.7969803 | set molar flow=false | molar flow=28.47243063 | isobaric=true
vaporizer | 2 | 3b | Exchange | 1725918.27 | other | 512.93881006 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=feedwater pump | outletStrConnected=true | outletProc=turbine | observed=false | set volume flow=false | volume flow=0.510323115 | set molar flow=false | molar flow=28.47243063 | isobaric=false
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | river | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.738604304 | CalcDim=false | set design=true | UA=104604.3672908 | DTmin=0
boiler | boiler | vaporizer | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.349081145 | CalcDim=false | set design=true | UA=1677.66136094 | DTmin=0
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=boiler | compType=HeatEx | ADesign_value=7500.00009 | eLambda=0
type=ext_tube | free_flow=100 | Dh=0.02 | length=1 | surf_fact=5 | fin=0.8 | pres_aval=false | DPArea=0.034143 | dPSing=0 | C1=0.0 | a_Re=0.0 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=40 | Dh=0.02 | length=100 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.041090 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=50999.98736 | eLambda=0
type=cond_ext_hor | free_flow=123.6 | Dh=0.02 | length=0.1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.737744 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=int_tube | free_flow=25.8 | Dh=0.016 | length=1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.033303 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=turbine | compType=Expansion | outletArea_value=0.04 | N_value=1500 | etaMax_value=0.92 | etaLim_value=0.85 | alphaBaumann_value=1 | etaIsentr_value=0.9 | Kh_value=90.0000 | tauMax_value=1000 | beta_value=30 | D_value=10 | stageNumber_value=1 | isChoked=false | isEtaConst=false | isPVR=false
PILOT
mCpRefrigBoiler=3177.965854412194 | mCpRefrigCond=1045856.4311763569 | Kh=90.0 | UAevap=1678.1800841646582 | UAcond=102979.88802706292 | mCpCalopBoiler=3136.6884865619495 | mCpCalopCond=75344.6661130274 | DeltaHevap=1725887.3566495979 | DeltaHcond=1045748.7601267067 | tauTurb=-680138.5965228912 | AdesignBoiler=7500.0000 | AcalculatedBoiler=7499.9303 | AdesignCond=51000.0000 | AcalculatedCond=51000.0245 | RVL=0.0 | DHcompr=8480.183010557656 | #technoBoiler=3steps=false:ADesign_value=7500.00009:@confHot=type=ext_tube:free_flow=100:Dh=0.02:length=1:surf_fact=5:fin=0.8:pres_aval=false:DPArea=0.034143:C1=0.0:a_Re=0.0:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=40:Dh=0.02:length=100:surf_fact=1:fin=1:pres_aval=false:DPArea=0.041090:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=50999.98736:@confHot=type=cond_ext_hor:free_flow=123.6:Dh=0.02:length=0.1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.737744:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=int_tube:free_flow=25.8:Dh=0.016:length=1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.033303:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#

## steamOffDesign_8
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | July 2, 2012 5:52:35 AM CEST
lang=fr | schem=steam power plant | pilotframe=Steam plant driver | unit m=kg/s
Project name | Simple steam plant | optimization=false | technodesign=true | thermocoupler=true
steam power plant
image=
Components | 0
PRESSURE SETTINGS | 0
name | value
COMPOUND GASES | 1
Gas name / Components | molar fraction | mass fraction
burnt gases | 5
CO2 | 0.0421611297 | 0.0652103215
H2O | 0.0811099829 | 0.0513534983
O2 | 0.119000221 | 0.133824666
N2 | 0.749100889 | 0.737497993
Ar | 0.00862777745 | 0.0121135218
POINTS | 8
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
1 | water | 25.57136 | 0.0347489881 | 0 | 107.19314547 | 107.18966001 | 0.00100304169 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-1 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
2 | water | 25.8953356 | 165 | 0 | 123.68021639 | 107.24818346 | 0.000995880784 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3b | water | 565 | 165 | 1 | 3473.16909837 | 3123.98520995 | 0.0211626599 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
4 | water | 26.57135 | 0.0347489881 | 0.841740035 | 2164.21128786 | 2047.94947619 | 33.45761072 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-0.0000000136629 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
hot gas | burnt gases | 1588.13284793 | 1 | 1 | 1893.52670461 | 1436.75174213 | 5.43847458 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
cooled gas | burnt gases | 1040.3950421 | 1 | 1 | 1177.65886622 | 880.92718448 | 3.83804177 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river inlet | water | 8 | 3 | 0 | 33.94011111 | 33.64011852 | 0.000999975316 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river outlet | water | 22.0039696 | 3 | 0 | 92.55813412 | 92.25752628 | 0.00100202614 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 10
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
river outlet | river outlet | river outlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=river | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=18.03647059 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river | river inlet | river outlet | Exchange | 1055124.41414293 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=river inlet | outletStrConnected=true | outletProc=river outlet | observed=false | set volume flow=false | volume flow=17.99955569 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river inlet | river inlet | river inlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=river | observed=false | set volume flow=false | volume flow=18.02860078 | set molar flow=false | molar flow=999.15183111 | isobaric=true
cooled gas | cooled gas | cooled gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=boiler | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=9210.28272902 | set molar flow=false | molar flow=84.3462831 | isobaric=true
boiler | hot gas | cooled gas | Exchange | -1718082.81214364 | purchased | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=hot gas | outletStrConnected=true | outletProc=cooled gas | observed=false | set volume flow=false | volume flow=13052.33899273 | set molar flow=false | molar flow=84.3462831 | isobaric=true
hot gas | hot gas | hot gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=boiler | observed=false | set volume flow=false | volume flow=12812.38795086 | set molar flow=false | molar flow=84.3462831 | isobaric=true
feedwater pump | 1 | 2 | Compression | 8456.86 | useful | 512.93879835 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=4748.34 | cooled=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=vaporizer | observed=false | k_polytr=1181.54751 | Q_value=0
turbine | 3b | 4 | Expansion | -671415.24 | useful | 512.93879835 | open_syst=true | set flow=true | rend=0.85737 | isentr=true | calc_direct=true | calc_press=true | press_ratio=4748.34 | cooled=false | comment= | inletStrConnected=true | inletProc=vaporizer | outletStrConnected=true | outletProc=condenser | observed=false | k_polytr=1.14931 | Q_value=0 | mechBalanced=false | mechBalancedCompr=
condenser | 4 | 1 | Exchange | -1055124.41 | other | 512.93879835 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=turbine | outletStrConnected=true | outletProc=feedwater pump | observed=false | set volume flow=false | volume flow=17161.70663748 | set molar flow=false | molar flow=28.47242998 | isobaric=true
vaporizer | 2 | 3b | Exchange | 1718082.8 | other | 512.93879835 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=feedwater pump | outletStrConnected=true | outletProc=turbine | observed=false | set volume flow=false | volume flow=0.510825893 | set molar flow=false | molar flow=28.47242998 | isobaric=false
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | river | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.754063092 | CalcDim=false | set design=true | UA=109320.47937095 | DTmin=0
boiler | boiler | vaporizer | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.350611096 | CalcDim=false | set design=true | UA=1686.36202731 | DTmin=0
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=boiler | compType=HeatEx | ADesign_value=7500.00029 | eLambda=0
type=ext_tube | free_flow=100 | Dh=0.02 | length=1 | surf_fact=5 | fin=0.8 | pres_aval=false | DPArea=0.034112 | dPSing=0 | C1=0.0 | a_Re=0.0 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=40 | Dh=0.02 | length=100 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.041090 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=50999.98194 | eLambda=0
type=cond_ext_hor | free_flow=123.6 | Dh=0.02 | length=0.1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.680647 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=int_tube | free_flow=25.8 | Dh=0.016 | length=1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.032504 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=turbine | compType=Expansion | outletArea_value=0.04 | N_value=1500 | etaMax_value=0.92 | etaLim_value=0.85 | alphaBaumann_value=1 | etaIsentr_value=0.9 | Kh_value=90.0000 | tauMax_value=1000 | beta_value=30 | D_value=10 | stageNumber_value=1 | isChoked=false | isEtaConst=false | isPVR=false
PILOT
mCpRefrigBoiler=3184.948077043602 | mCpRefrigCond=1046603.7564303252 | Kh=90.0 | UAevap=1686.591332251952 | UAcond=107369.96981191111 | mCpCalopBoiler=3136.6884865619495 | mCpCalopCond=75344.6661130274 | DeltaHevap=1718052.2256236395 | DeltaHcond=1046636.9847276398 | tauTurb=-671415.2408959997 | AdesignBoiler=7500.0000 | AcalculatedBoiler=7498.9958 | AdesignCond=51000.0000 | AcalculatedCond=50999.9522 | RVL=0.0 | DHcompr=8487.445658680717 | #technoBoiler=3steps=false:ADesign_value=7500.00029:@confHot=type=ext_tube:free_flow=100:Dh=0.02:length=1:surf_fact=5:fin=0.8:pres_aval=false:DPArea=0.034112:C1=0.0:a_Re=0.0:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=40:Dh=0.02:length=100:surf_fact=1:fin=1:pres_aval=false:DPArea=0.041090:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=50999.98194:@confHot=type=cond_ext_hor:free_flow=123.6:Dh=0.02:length=0.1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.680647:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=int_tube:free_flow=25.8:Dh=0.016:length=1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.032504:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#

## steamOffDesign_12
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | July 1, 2012 9:45:10 PM CEST
lang=fr | schem=steam power plant | pilotframe=Steam plant driver | unit m=kg/s
Project name | Simple steam plant | optimization=false | technodesign=true | thermocoupler=true
steam power plant
image=
Components | 0
PRESSURE SETTINGS | 0
name | value
COMPOUND GASES | 1
Gas name / Components | molar fraction | mass fraction
burnt gases | 5
CO2 | 0.0421611297 | 0.0652103215
H2O | 0.0811099829 | 0.0513534983
O2 | 0.119000221 | 0.133824666
N2 | 0.749100889 | 0.737497993
Ar | 0.00862777745 | 0.0121135218
POINTS | 8
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
1 | water | 29.24715 | 0.0430204664 | 0 | 122.55508909 | 122.55076949 | 0.00100408023 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-1 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
2 | water | 29.61471036 | 165 | 0 | 139.05899089 | 122.60872631 | 0.000996985732 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3b | water | 565 | 165 | 1 | 3473.16909837 | 3123.98520995 | 0.0211626599 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
4 | water | 30.24715 | 0.0430204664 | 0.84525444 | 2180.78964483 | 2062.64017512 | 27.46354924 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
hot gas | burnt gases | 1579.02279249 | 1 | 1 | 1881.35723482 | 1427.24413563 | 5.41185595 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
cooled gas | burnt gases | 1033.39809551 | 1 | 1 | 1168.77624135 | 874.08899451 | 3.81759742 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river inlet | water | 12 | 3 | 0 | 50.70612711 | 50.40603551 | 0.00100030534 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river outlet | water | 26.0240865 | 3 | 0 | 109.35881178 | 109.05790303 | 0.00100302915 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 10
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
river outlet | river outlet | river outlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=river | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=18.05452473 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river | river inlet | river outlet | Exchange | 1055748.3239936 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=river inlet | outletStrConnected=true | outletProc=river outlet | observed=false | set volume flow=false | volume flow=18.00549612 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river inlet | river inlet | river inlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=river | observed=false | set volume flow=false | volume flow=18.02860078 | set molar flow=false | molar flow=999.15183111 | isobaric=true
cooled gas | cooled gas | cooled gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=boiler | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=9126.31445312 | set molar flow=false | molar flow=84.3462831 | isobaric=true
boiler | hot gas | cooled gas | Exchange | -1710194.38433896 | purchased | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=hot gas | outletStrConnected=true | outletProc=cooled gas | observed=false | set volume flow=false | volume flow=12988.45427367 | set molar flow=false | molar flow=84.3462831 | isobaric=true
hot gas | hot gas | hot gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=boiler | observed=false | set volume flow=false | volume flow=12812.38795086 | set molar flow=false | molar flow=84.3462831 | isobaric=true
feedwater pump | 1 | 2 | Compression | 8465.49 | useful | 512.93878098 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=3835.38 | cooled=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=vaporizer | observed=false | k_polytr=1163.77413 | Q_value=0
turbine | 3b | 4 | Expansion | -662911.54 | useful | 512.93878098 | open_syst=true | set flow=true | rend=0.85912 | isentr=true | calc_direct=true | calc_press=true | press_ratio=3835.38 | cooled=false | comment= | inletStrConnected=true | inletProc=vaporizer | outletStrConnected=true | outletProc=condenser | observed=false | k_polytr=1.15117 | Q_value=0 | mechBalanced=false | mechBalancedCompr=
condenser | 4 | 1 | Exchange | -1055748.32 | other | 512.93878098 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=turbine | outletStrConnected=true | outletProc=feedwater pump | observed=false | set volume flow=false | volume flow=14087.11946608 | set molar flow=false | molar flow=28.47242901 | isobaric=true
vaporizer | 2 | 3b | Exchange | 1710194.37 | other | 512.93878098 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=feedwater pump | outletStrConnected=true | outletProc=turbine | observed=false | set volume flow=false | volume flow=0.511392646 | set molar flow=false | molar flow=28.47242901 | isobaric=false
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | river | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.768563118 | CalcDim=false | set design=true | UA=114060.11409435 | DTmin=0
boiler | boiler | vaporizer | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.352150414 | CalcDim=false | set design=true | UA=1695.11727439 | DTmin=0
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=boiler | compType=HeatEx | ADesign_value=7499.99997 | eLambda=0
type=ext_tube | free_flow=100 | Dh=0.02 | length=1 | surf_fact=5 | fin=0.8 | pres_aval=false | DPArea=0.034082 | dPSing=0 | C1=0.0 | a_Re=0.0 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=40 | Dh=0.02 | length=100 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.041090 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=50999.99616 | eLambda=0
type=cond_ext_hor | free_flow=123.6 | Dh=0.02 | length=0.1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.629393 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=int_tube | free_flow=25.8 | Dh=0.016 | length=1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.031773 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=turbine | compType=Expansion | outletArea_value=0.04 | N_value=1500 | etaMax_value=0.92 | etaLim_value=0.85 | alphaBaumann_value=1 | etaIsentr_value=0.9 | Kh_value=90.0000 | tauMax_value=1000 | beta_value=30 | D_value=10 | stageNumber_value=1 | isChoked=false | isEtaConst=false | isPVR=false
PILOT
mCpRefrigBoiler=3192.0764502314682 | mCpRefrigCond=1047329.3022774055 | Kh=90.0 | UAevap=1695.0482202666788 | UAcond=111874.22243414643 | mCpCalopBoiler=3136.6884865619495 | mCpCalopCond=75344.6661130274 | DeltaHevap=1710164.0638566401 | DeltaHcond=1047252.519664991 | tauTurb=-662911.5441916492 | AdesignBoiler=7500.0000 | AcalculatedBoiler=7499.6918 | AdesignCond=51000.0000 | AcalculatedCond=50999.9897 | RVL=0.0 | DHcompr=8495.807138085233 | #technoBoiler=3steps=false:ADesign_value=7499.99997:@confHot=type=ext_tube:free_flow=100:Dh=0.02:length=1:surf_fact=5:fin=0.8:pres_aval=false:DPArea=0.034082:C1=0.0:a_Re=0.0:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=40:Dh=0.02:length=100:surf_fact=1:fin=1:pres_aval=false:DPArea=0.041090:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=50999.99616:@confHot=type=cond_ext_hor:free_flow=123.6:Dh=0.02:length=0.1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.629393:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=int_tube:free_flow=25.8:Dh=0.016:length=1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.031773:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#

## steamOffDesign_16
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | July 1, 2012 9:45:40 PM CEST
lang=fr | schem=steam power plant | pilotframe=Steam plant driver | unit m=kg/s
Project name | Simple steam plant | optimization=false | technodesign=true | thermocoupler=true
steam power plant
image=
Components | 0
PRESSURE SETTINGS | 0
name | value
COMPOUND GASES | 1
Gas name / Components | molar fraction | mass fraction
burnt gases | 5
CO2 | 0.0421611297 | 0.0652103215
H2O | 0.0811099829 | 0.0513534983
O2 | 0.119000221 | 0.133824666
N2 | 0.749100889 | 0.737497993
Ar | 0.00862777745 | 0.0121135218
POINTS | 8
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
1 | water | 32.94533 | 0.0530190235 | 0 | 138.00865602 | 138.00332628 | 0.00100525109 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-1 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
2 | water | 33.35543686 | 165 | 0 | 154.53144833 | 138.06098397 | 0.000998209961 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3b | water | 565 | 165 | 1 | 3473.16909837 | 3123.98520995 | 0.0211626599 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
4 | water | 33.94533 | 0.0530190235 | 0.848569477 | 2196.85422247 | 2076.82965516 | 22.63801922 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
hot gas | burnt gases | 1569.9586349 | 1 | 1 | 1869.25597478 | 1417.79132801 | 5.38537142 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
cooled gas | burnt gases | 1026.46431461 | 1 | 1 | 1159.9818596 | 867.3205913 | 3.79733764 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river inlet | water | 16 | 3 | 0 | 67.45075226 | 67.15049715 | 0.00100085037 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river outlet | water | 30.03601564 | 3 | 0 | 126.12084574 | 125.81958954 | 0.00100418732 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 10
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
river outlet | river outlet | river outlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=river | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=18.07537185 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river | river inlet | river outlet | Exchange | 1056061.68256075 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=river inlet | outletStrConnected=true | outletProc=river outlet | observed=false | set volume flow=false | volume flow=18.01530668 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river inlet | river inlet | river inlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=river | observed=false | set volume flow=false | volume flow=18.02860078 | set molar flow=false | molar flow=999.15183111 | isobaric=true
cooled gas | cooled gas | cooled gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=boiler | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=9077.7591824 | set molar flow=false | molar flow=84.3462831 | isobaric=true
boiler | hot gas | cooled gas | Exchange | -1702257.87644192 | purchased | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=hot gas | outletStrConnected=true | outletProc=cooled gas | observed=false | set volume flow=false | volume flow=12924.8914156 | set molar flow=false | molar flow=84.3462831 | isobaric=true
hot gas | hot gas | hot gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=boiler | observed=false | set volume flow=false | volume flow=12812.38795086 | set molar flow=false | molar flow=84.3462831 | isobaric=true
feedwater pump | 1 | 2 | Compression | 8475.18 | useful | 512.93875547 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=3112.09 | cooled=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=vaporizer | observed=false | k_polytr=1144.26723 | Q_value=0
turbine | 3b | 4 | Expansion | -654671.37 | useful | 512.93875547 | open_syst=true | set flow=true | rend=0.86124 | isentr=true | calc_direct=true | calc_press=true | press_ratio=3112.09 | cooled=false | comment= | inletStrConnected=true | inletProc=vaporizer | outletStrConnected=true | outletProc=condenser | observed=false | k_polytr=1.1531 | Q_value=0 | mechBalanced=false | mechBalancedCompr=
condenser | 4 | 1 | Exchange | -1056061.68 | other | 512.93875547 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=turbine | outletStrConnected=true | outletProc=feedwater pump | observed=false | set volume flow=false | volume flow=11611.91740566 | set molar flow=false | molar flow=28.4724276 | isobaric=true
vaporizer | 2 | 3b | Exchange | 1702257.87 | other | 512.93875547 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=feedwater pump | outletStrConnected=true | outletProc=turbine | observed=false | set volume flow=false | volume flow=0.512020575 | set molar flow=false | molar flow=28.4724276 | isobaric=false
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | river | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.782154223 | CalcDim=false | set design=true | UA=118813.30001909 | DTmin=0
boiler | boiler | vaporizer | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.353698548 | CalcDim=false | set design=true | UA=1703.92422984 | DTmin=0
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=boiler | compType=HeatEx | ADesign_value=7499.99999 | eLambda=0
type=ext_tube | free_flow=100 | Dh=0.02 | length=1 | surf_fact=5 | fin=0.8 | pres_aval=false | DPArea=0.034051 | dPSing=0 | C1=0.0 | a_Re=0.0 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=40 | Dh=0.02 | length=100 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.041090 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=50999.99840 | eLambda=0
type=cond_ext_hor | free_flow=123.6 | Dh=0.02 | length=0.1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.583320 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=int_tube | free_flow=25.8 | Dh=0.016 | length=1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.031103 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=turbine | compType=Expansion | outletArea_value=0.04 | N_value=1500 | etaMax_value=0.92 | etaLim_value=0.85 | alphaBaumann_value=1 | etaIsentr_value=0.9 | Kh_value=90.0000 | tauMax_value=1000 | beta_value=30 | D_value=10 | stageNumber_value=1 | isChoked=false | isEtaConst=false | isPVR=false
PILOT
mCpRefrigBoiler=3199.3476249514224 | mCpRefrigCond=1047703.1907648874 | Kh=90.0 | UAevap=1703.5482988820415 | UAcond=116360.20203077959 | mCpCalopBoiler=3136.6884865619495 | mCpCalopCond=75344.6661130274 | DeltaHevap=1702227.855724819 | DeltaHcond=1047556.4882361635 | tauTurb=-654671.3674886555 | AdesignBoiler=7500.0000 | AcalculatedBoiler=7500.0129 | AdesignCond=51000.0000 | AcalculatedCond=50999.9956 | RVL=0.0 | DHcompr=8505.198187379552 | #technoBoiler=3steps=false:ADesign_value=7499.99999:@confHot=type=ext_tube:free_flow=100:Dh=0.02:length=1:surf_fact=5:fin=0.8:pres_aval=false:DPArea=0.034051:C1=0.0:a_Re=0.0:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=40:Dh=0.02:length=100:surf_fact=1:fin=1:pres_aval=false:DPArea=0.041090:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=50999.99840:@confHot=type=cond_ext_hor:free_flow=123.6:Dh=0.02:length=0.1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.583320:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=int_tube:free_flow=25.8:Dh=0.016:length=1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.031103:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#

## steamOffDesign_20
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | July 1, 2012 9:49:10 PM CEST
lang=fr | schem=steam power plant | pilotframe=Steam plant driver | unit m=kg/s
Project name | Simple steam plant | optimization=false | technodesign=true | thermocoupler=true
steam power plant
image=
Components | 0
PRESSURE SETTINGS | 0
name | value
COMPOUND GASES | 1
Gas name / Components | molar fraction | mass fraction
burnt gases | 5
CO2 | 0.0421611297 | 0.0652103215
H2O | 0.0811099829 | 0.0513534983
O2 | 0.119000221 | 0.133824666
N2 | 0.749100889 | 0.737497993
Ar | 0.00862777745 | 0.0121135218
POINTS | 8
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
1 | water | 36.66328 | 0.0650426637 | 0 | 153.54457342 | 153.53802656 | 0.0010065486 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-1 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
2 | water | 37.11505466 | 165 | 0 | 170.08774608 | 153.5951914 | 0.000999548769 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3b | water | 565 | 165 | 1 | 3473.16909837 | 3123.98520995 | 0.0211626599 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
4 | water | 37.66328 | 0.0650426637 | 0.851654106 | 2212.32677265 | 2090.44659956 | 18.73849657 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
hot gas | burnt gases | 1560.94468062 | 1 | 1 | 1857.22864455 | 1408.39778132 | 5.35903359 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
cooled gas | burnt gases | 1019.59668412 | 1 | 1 | 1151.27934206 | 860.62472385 | 3.77727114 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river inlet | water | 20 | 3 | 0 | 84.18056832 | 83.88009164 | 0.00100158893 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river outlet | water | 34.04024112 | 3 | 0 | 142.8488518 | 142.54720494 | 0.00100548953 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 10
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
river outlet | river outlet | river outlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=river | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=18.09881159 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river | river inlet | river outlet | Exchange | 1056029.10259439 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=river inlet | outletStrConnected=true | outletProc=river outlet | observed=false | set volume flow=false | volume flow=18.02860078 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river inlet | river inlet | river inlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=river | observed=false | set volume flow=false | volume flow=18.02860078 | set molar flow=false | molar flow=999.15183111 | isobaric=true
cooled gas | cooled gas | cooled gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=boiler | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=9029.67547923 | set molar flow=false | molar flow=84.3462831 | isobaric=true
boiler | hot gas | cooled gas | Exchange | -1694278.32596534 | purchased | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=hot gas | outletStrConnected=true | outletProc=cooled gas | observed=false | set volume flow=false | volume flow=12861.68061074 | set molar flow=false | molar flow=84.3462831 | isobaric=true
hot gas | hot gas | hot gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=boiler | observed=false | set volume flow=false | volume flow=12812.38795086 | set molar flow=false | molar flow=84.3462831 | isobaric=true
feedwater pump | 1 | 2 | Compression | 8485.63 | useful | 512.93871833 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=2536.8 | cooled=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=vaporizer | observed=false | k_polytr=1123.24536 | Q_value=0
turbine | 3b | 4 | Expansion | -646734.84 | useful | 512.93871833 | open_syst=true | set flow=true | rend=0.86379 | isentr=true | calc_direct=true | calc_press=true | press_ratio=2536.8 | cooled=false | comment= | inletStrConnected=true | inletProc=vaporizer | outletStrConnected=true | outletProc=condenser | observed=false | k_polytr=1.15511 | Q_value=0 | mechBalanced=false | mechBalancedCompr=
condenser | 4 | 1 | Exchange | -1056029.1 | other | 512.93871833 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=turbine | outletStrConnected=true | outletProc=feedwater pump | observed=false | set volume flow=false | volume flow=9611.70041577 | set molar flow=false | molar flow=28.47242554 | isobaric=true
vaporizer | 2 | 3b | Exchange | 1694278.32 | other | 512.93871833 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=feedwater pump | outletStrConnected=true | outletProc=turbine | observed=false | set volume flow=false | volume flow=0.512707264 | set molar flow=false | molar flow=28.47242554 | isobaric=false
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | river | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.794883007 | CalcDim=false | set design=true | UA=123570.47917963 | DTmin=0
boiler | boiler | vaporizer | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.355254936 | CalcDim=false | set design=true | UA=1712.77996034 | DTmin=0
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=boiler | compType=HeatEx | ADesign_value=7500.00073 | eLambda=0
type=ext_tube | free_flow=100 | Dh=0.02 | length=1 | surf_fact=5 | fin=0.8 | pres_aval=false | DPArea=0.034020 | dPSing=0 | C1=0.0 | a_Re=0.0 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=40 | Dh=0.02 | length=100 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.041090 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=51000.01907 | eLambda=0
type=cond_ext_hor | free_flow=123.6 | Dh=0.02 | length=0.1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.541842 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=int_tube | free_flow=25.8 | Dh=0.016 | length=1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.030489 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=turbine | compType=Expansion | outletArea_value=0.04 | N_value=1500 | etaMax_value=0.92 | etaLim_value=0.85 | alphaBaumann_value=1 | etaIsentr_value=0.9 | Kh_value=90.0000 | tauMax_value=1000 | beta_value=30 | D_value=10 | stageNumber_value=1 | isChoked=false | isEtaConst=false | isPVR=false
PILOT
mCpRefrigBoiler=3206.758749505302 | mCpRefrigCond=1047542.5239564959 | Kh=90.0 | UAevap=1712.7818479597609 | UAcond=121097.03447227461 | mCpCalopBoiler=3132.0619423099415 | mCpCalopCond=75239.42047707413 | DeltaHevap=1694248.3842735363 | DeltaHcond=1047513.5428539809 | tauTurb=-646734.8414195554 | AdesignBoiler=7500.0000 | AcalculatedBoiler=7499.9983 | AdesignCond=51000.0000 | AcalculatedCond=50999.9935 | RVL=0.0 | DHcompr=8515.554694960803 | #technoBoiler=3steps=false:ADesign_value=7500.00073:@confHot=type=ext_tube:free_flow=100:Dh=0.02:length=1:surf_fact=5:fin=0.8:pres_aval=false:DPArea=0.034020:C1=0.0:a_Re=0.0:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=40:Dh=0.02:length=100:surf_fact=1:fin=1:pres_aval=false:DPArea=0.041090:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=51000.01907:@confHot=type=cond_ext_hor:free_flow=123.6:Dh=0.02:length=0.1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.541842:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=int_tube:free_flow=25.8:Dh=0.016:length=1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.030489:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#

## steamOffDesign_24
THERMOPTIM SOFTWARE;proj;version=2.70 | Copyright R. Gicquel 1999-2011
code=Univ | July 1, 2012 9:50:37 PM CEST
lang=fr | schem=steam power plant | pilotframe=Steam plant driver | unit m=kg/s
Project name | Simple steam plant | optimization=false | technodesign=true | thermocoupler=true
steam power plant
image=
Components | 0
PRESSURE SETTINGS | 0
name | value
COMPOUND GASES | 1
Gas name / Components | molar fraction | mass fraction
burnt gases | 5
CO2 | 0.0421611297 | 0.0652103215
H2O | 0.0811099829 | 0.0513534983
O2 | 0.119000221 | 0.133824666
N2 | 0.749100889 | 0.737497993
Ar | 0.00862777745 | 0.0121135218
POINTS | 8
name | substance name | T (°C) | P (bar) | quality | h (kJ/kg) | u (kJ/kg) | V (m3/kg)
1 | water | 40.39849 | 0.0794284039 | 0 | 169.15373515 | 169.14572902 | 0.00100796773 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=-1 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
2 | water | 40.89135351 | 165 | 0 | 185.71900642 | 169.20253707 | 0.00100099814 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
3b | water | 565 | 165 | 1 | 3473.16909837 | 3123.98520995 | 0.0211626599 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
4 | water | 41.39849 | 0.0794284039 | 0.85447393 | 2227.12224644 | 2103.41359958 | 15.57486249 | open_syst=true | calc_pT=true | set_Tsat=true | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
hot gas | burnt gases | 1551.985311 | 1 | 1 | 1845.28105138 | 1399.06802262 | 5.33285524 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
cooled gas | burnt gases | 1012.79843381 | 1 | 1 | 1142.67260495 | 854.00436466 | 3.75740736 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river inlet | water | 24 | 3 | 0 | 100.90059296 | 100.59984186 | 0.0010025037 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
river outlet | water | 38.03697203 | 3 | 0 | 159.54568298 | 159.24360499 | 0.00100692663 | open_syst=true | calc_pT=true | set_Tsat=false | DTsat=0 | set_psat=false | set_p=false | Pvalue= | calc_vT=true | press_corr=1 | observed=false
PROCESSES | 10
name | inlet point | outlet point | type | m ?h | type_ener | flow rate
river outlet | river outlet | river outlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=river | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=18.12467931 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river | river inlet | river outlet | Exchange | 1055611.6202975 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=river inlet | outletStrConnected=true | outletProc=river outlet | observed=false | set volume flow=false | volume flow=18.04506656 | set molar flow=false | molar flow=999.15183111 | isobaric=true
river inlet | river inlet | river inlet | Exchange | 0 | other | 18000 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=river | observed=false | set volume flow=false | volume flow=18.02860078 | set molar flow=false | molar flow=999.15183111 | isobaric=true
cooled gas | cooled gas | cooled gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=boiler | outletStrConnected=false | outletProc= | observed=false | set volume flow=false | volume flow=9016.74414698 | set molar flow=false | molar flow=84.3462831 | isobaric=true
boiler | hot gas | cooled gas | Exchange | -1686260.2714205 | purchased | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=true | comment= | inletStrConnected=true | inletProc=hot gas | outletStrConnected=true | outletProc=cooled gas | observed=false | set volume flow=false | volume flow=12798.85258349 | set molar flow=false | molar flow=84.3462831 | isobaric=true
hot gas | hot gas | hot gas | Exchange | 0 | other | 2400 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=false | inletProc= | outletStrConnected=true | outletProc=boiler | observed=false | set volume flow=false | volume flow=12812.38795086 | set molar flow=false | molar flow=84.3462831 | isobaric=true
feedwater pump | 1 | 2 | Compression | 8496.97 | useful | 512.93866476 | open_syst=true | set flow=false | rend=1 | isentr=true | calc_direct=true | calc_press=true | press_ratio=2077.34 | cooled=false | comment= | inletStrConnected=true | inletProc=condenser | outletStrConnected=true | outletProc=vaporizer | observed=false | k_polytr=1100.93484 | Q_value=0
turbine | 3b | 4 | Expansion | -639145.61 | useful | 512.93866476 | open_syst=true | set flow=true | rend=0.86684 | isentr=true | calc_direct=true | calc_press=true | press_ratio=2077.34 | cooled=false | comment= | inletStrConnected=true | inletProc=vaporizer | outletStrConnected=true | outletProc=condenser | observed=false | k_polytr=1.15719 | Q_value=0 | mechBalanced=false | mechBalancedCompr=
condenser | 4 | 1 | Exchange | -1055611.62 | other | 512.93866476 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=turbine | outletStrConnected=true | outletProc=feedwater pump | observed=false | set volume flow=false | volume flow=7988.94917014 | set molar flow=false | molar flow=28.47242256 | isobaric=true
vaporizer | 2 | 3b | Exchange | 1686260.26 | other | 512.93866476 | open_syst=true | set flow=false | calc_direct=false | min pinch DT=0 | pinch fluid=false | comment= | inletStrConnected=true | inletProc=feedwater pump | outletStrConnected=true | outletProc=turbine | observed=false | set volume flow=false | volume flow=0.513450651 | set molar flow=false | molar flow=28.47242256 | isobaric=false
NODES | 0
name | process | type | flow rate
HEAT EXCHANGERS | 2
name | hot fluid | cold fluid | type
condenser | condenser | river | contre_courant | set Tce=true | set Tcs=true | set Mc=true | set Tfe=true | set Tfs=false | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.806792545 | CalcDim=false | set design=true | UA=128321.95331703 | DTmin=0
boiler | boiler | vaporizer | contre_courant | set Tce=true | set Tcs=false | set Mc=true | set Tfe=true | set Tfs=true | set Mf=true | set min Pinch=false | set eff=false | epsilon=0.356818896 | CalcDim=false | set design=true | UA=1721.68065205 | DTmin=0
THERMOCOUPLERS | 0
name | hot fluid | cold fluid | type
TECHNOLOGICAL DESIGN PARAMETERS
nb TechnoDesign | 3
component=boiler | compType=HeatEx | ADesign_value=7499.99606 | eLambda=0
type=ext_tube | free_flow=100 | Dh=0.02 | length=1 | surf_fact=5 | fin=0.8 | pres_aval=false | DPArea=0.033990 | dPSing=0 | C1=0.0 | a_Re=0.0 | b_Pr=0.0 | c_Visc=0.0 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=evap | free_flow=40 | Dh=0.02 | length=100 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.041090 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=condenser | compType=HeatEx | ADesign_value=51000.00791 | eLambda=0
type=cond_ext_hor | free_flow=123.6 | Dh=0.02 | length=0.1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.504442 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
type=int_tube | free_flow=25.8 | Dh=0.016 | length=1 | surf_fact=1 | fin=1 | pres_aval=false | DPArea=0.029924 | dPSing=0 | C1=0.023000000000000003 | a_Re=0.8 | b_Pr=0.4 | c_Visc=0.14 | C2=0.31 | d_Re=-0.25 | RR=0.0010 | Kh=1.0 | colebrook=true | laminar=false
component=turbine | compType=Expansion | outletArea_value=0.04 | N_value=1500 | etaMax_value=0.92 | etaLim_value=0.85 | alphaBaumann_value=1 | etaIsentr_value=0.9 | Kh_value=90.0000 | tauMax_value=1000 | beta_value=30 | D_value=10 | stageNumber_value=1 | isChoked=false | isEtaConst=false | isPVR=false
PILOT
mCpRefrigBoiler=3214.307205425733 | mCpRefrigCond=1046996.5348465979 | Kh=90.0 | UAevap=1721.366200130831 | UAcond=125621.33693363905 | mCpCalopBoiler=3132.0619423099415 | mCpCalopCond=75239.42047707413 | DeltaHevap=1686230.4108554348 | DeltaHcond=1047084.8038897939 | tauTurb=-639145.6069656409 | AdesignBoiler=7500.0000 | AcalculatedBoiler=7499.8942 | AdesignCond=51000.0000 | AcalculatedCond=50999.8030 | RVL=0.0 | DHcompr=8526.81608284998 | #technoBoiler=3steps=false:ADesign_value=7499.99606:@confHot=type=ext_tube:free_flow=100:Dh=0.02:length=1:surf_fact=5:fin=0.8:pres_aval=false:DPArea=0.033990:C1=0.0:a_Re=0.0:b_Pr=0.0:c_Visc=0.0:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::@confCold=type=evap:free_flow=40:Dh=0.02:length=100:surf_fact=1:fin=1:pres_aval=false:DPArea=0.041090:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::# | #technoCond=3steps=false:ADesign_value=51000.00791:@confHot=type=cond_ext_hor:free_flow=123.6:Dh=0.02:length=0.1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.504442:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false:pressure_factor=1::@confCold=type=int_tube:free_flow=25.8:Dh=0.016:length=1:surf_fact=1:fin=1:pres_aval=false:DPArea=0.029924:C1=0.023000000000000003:a_Re=0.8:b_Pr=0.4:c_Visc=0.14:C2=0.31:d_Re=-0.25:RR=0.0010:Kh=1.0:colebrook=true:laminar=false::#